Coated line pipe specification

- scope and definitions

- process of manufacturing and material

- line pipe inspection

- hydrostatic tests

- non-destructive inspection

- workmanship ,visual inspection and defect repair

- line pipe dimensions and tolerance

- first day manufacturing tests

- coating

- marking

- line pipe handling and shipping

Section 1

General data and definitions

- scope and definitions

- Scope

This specification SHALL be used for ordering the described quantities below (meter) of, submerged-arc-welded (SAW) line pipe ( as detailed hereafter)for Syrian gas COMPANY, ARAB GAS PIPELINE PROJECT- PHASE II  manufactured according to API 5L forty second edition .

The intent of this specification is to provide the specific line pipe to avoid any confusion with manufacturers

Detailed information will be described  below.

- discrepancy and  priority

In case of conflict between documents related to the Inquiry or purchase Order, the following priorities SHALL be applied:

- This specification.

- API Specification 5 L forty second editions.

- definitions

For the purpose of this specification, the following definitions SHALL be considered:

- SHALL:

The word "SHALL" is to be understood as mandatory.

- SHOULD:

The word SHOULD is to be understood as strongly recommended complying with the requirements of this specification.

- COMPANY

The COMPANY means The Syrian gas COMPANY or its authorized representatives performing work on behalf of Syrian gas COMPANY.

- CONTRACTOR

- The CONTRACTOR, if any, selected by the COMPANY to procure and supply the required quantity of the line pipe according to this specification for the "ARAB GAS PIPELINE PROJECT- PHASE  II

- PROJECT

- The PROJECT means when this word used the:

- "ARAB GAS PIPELINE PROJECT- PHASE  II

- PURCHASER:  :

It means CONTRACTOR which is full responsible to procure and supply to the site line pipe subject of RFQ to Syrian gas COMPANY  after the COMPANY approval of his purchase order

- VENDOR:

- It means the MANUFACTURER of the line pipe included in COMPANY vendor list and chosen by CONTRACTOR and approved by COMPANY.

- INSPECTOR:

Is, the individual(s) designated by the CONTRACTOR and approved by the COMPANY as third party to act on PURCHASER’s behalf for all matters relating to Quality Control, Testing, and Acceptance of the work described in this Specification.

- General data

This specification SHALL be followed by manufacturer to provide the required PROJECT line pipe according to the following tables:

- 36 inch line pipe:

| Reference | API 5L forty second edition January 2000 |  |  |
| --- | --- | --- | --- |
| Grade | X70 |  |  |
| Product specification level | PSL2 |  |  |
| Process of manufacturing | SAW |  |  |
| out side diameter (inch ) | 36 |  |  |
| out side diameter (mm ) | 914 |  |  |
| Quantities(meter) | 140000 | 40000 | 10000 |
| Wall thicknesses (inch) | 0.406 | 0.469 | 0.562 |
| Wall thicknesses (mm) | 10.3 | 11.9 | 14.3 |
| Coating | Three layers 3mm PE density 950 kg/m3 |  |  |
| End preparation | Plain beveled according to API 5L par.7.9.3 |  |  |

Section 2

Process of manufacturing and material

- process of manufacturing and material

  - Process of Manufacture.

- The line pipe SHALL be manufactured according to the following:
API 5L X70 submerged arc welding process for 36" line pipe

  - Product specification level.

- The line pipe SHALL be manufactured according to PSL 2.

  - Out side diameter

- The purchased out side diameter shall be as the following:

- 36 “(thirty six) inch= 914mm for 190 km line pipe

  - Quantities and wall thicknesses :

- CONTRACTOR SHALL purchase, and procure, to the project site  and/or to company nominated ware houses the required quantities of the line pipe according to this specification as the following:

    - :for the 36" as the following :

- - 180000 meter(two hundred and eighty thousand meter of 0.406” wall thickness as listed in table 1.4.1 above

- -40000 meter(fifty four thousand meter of 0.469” wall thickness as listed in table 1.4.1 above

- - 10000 meter(six thousand meter of 0.562” wall thickness as listed in table 1.4.1 above

- This quantities shall be handed over directly to the company warehouse.

  - end preparation

- The end of line pipe SHALL be plain standard beveled end according to the API 5L para7.9.3 or this illustrated in ANSI B16.25 -1992

- The pipe ends SHALL be machined square to the pipe axis, within the API Spec 5L tolerance of 1.5 mm.

- Two pipes may be selected at random by inspection at least once during each working shift and laid in horizontally aligned V blocks or rolls with their ends butted together.

- The gap between the pipes should be measured by means of a taper gauge and SHALL not exceed 3.2mm at any position when one pipe is rotated.

- Each pipe should then be turned end for end and the gap SHALL be measured again.

- The bevel and the root face dimensions SHALL be rechecked after coating and prior to shipment.

- The end bevel SHALL be protected by inside metallic end protector and covered with external polyethylene caps strong enough to protect the pipe while transportation and to keep it clean from dirt’s, dust and rust

  - coating

- The line pipe SHALL be coated with 3 mm of polyethylene coating with 950kg/m3 density

  - Manufacturing procedure and welding procedure.

- The manufacturing procedure used for submerged arc welding line pipe SHALL be submitted to the COMPANY in accordance with the following:

- CONTRACTOR SHALL submit the following information for COMPANY's approval.

- The COMPANY may, with discretion, accept the results of previously authenticated tests, and may also accept a manufacturing procedure specification previously accepted for a similar order.

- The CONTRACTOR SHALL submit a specification of the manufacturing procedure, together with the results of the completed welding procedure qualification tests, for acceptance by COMPANY prior to commencement of production.

- The COMPANY reserves the right to require re qualification in the case of any change in the procedure specification.

- The procedure specification SHALL include, but not be limited to the following information:

- Manufacturing procedure.

- The manufacturing procedure for the submerged arc welded line pipe of the project SHALL include but limited to the following:

- Materials quality.

- Method of plate forming.

- Method and degree of cold expansion.

- Method of straightening, sizing and hydrostatic testing.

- Detailed quality plan covering quality control, inspection procedures and documentation.

- Steelmaking route, desulphurization techniques, inclusion shape control, method of monitoring shape control, de-oxidation practice.

- Suitability of material for field welding.

- Details of heat treatment (as rolled, normalized tempered or quenched).

- Welding procedure.

- Welding   procedure.

Welding procedure for submerged arc welded line pipe will include but not limited to the following:

- Joint design, clamping and tack welding

- Brand name, classification, size and grade of filler metal.

- Speed of welding.

- Electrical characteristics of welding (ampere, voltage and heat input)

- Number of weld passes.

- Limit of internal and external weld reinforcement

The submitted procedure and any agreed modification thereof SHALL be followed strictly as qualified in the production of pipes.

- Welding Procedure Qualification

For qualification of the welding procedure, the following tests SHALL be executed on a full length test weld made in accordance with the manufacturing procedure specification

At Least 48 hours after completion of the test weld the CONTRACTOR SHALL submit the test result for the COMPANY which include but not limited to the following:

- NDT

- Ultrasonic Examination

The weld seam SHALL be examined in accordance with Par. 9.7.4 of API Spec 5L.

- Radiographic Examination

The weld seam of pipe SHALL be examined in accordance with clauses 9.7.3.1 to 9.7.3.12 of API 5L over the entire length.

- Dye Check or Magnetic Particle Inspection

The weld seams procedure sample pipe SHALL be subjected to dye check or magnetic particle inspection in order to check for defects in the weld material at both surfaces throughout their full length in order to check on longitudinal and transverse surface defects in the weld material. Dye check materials and checking procedure SHALL have prior approval of INSPECTOR.

Cracks are unacceptable.

- Mechanical tests

- Tensile test

One specimen of the all weld seam SHALL be subjected to an all-weld tensile test in order to check the quality of the welding procedure.

Test results SHALL meet the minimum specified requirement of the plate with regard to yield, tensile strength and elongation stated in the table 3B.

- Bending Tests

- The specimen SHALL be consider accepted when root, face and side bend test accepted according to API 1104 requirements

- Macro graphic, Micrographic and Hardness inspection

- A specimen SHALL be taken from the weld seam and subjected to micrographic, micrographic and hardness inspection, as required by PLCP rev 2 (pipe line construction practice)

- Impact (or fracture toughness) Testing

- According to section 3

When these entire specimens meet the stated requirement that meet the welding procedure is acceptable

- repair-welding procedure and welder performance tests

- general

The preheating temperature SHALL be in accordance with the welding procedures. All repairs welding if any SHALL be performed to pre-qualified procedures by qualified welders/operators.

- Repair-Welding Procedure Tests.

Charpy  impact  tests SHALL  be  part  of  the repair welding procedure tests and SHALL  be  carried  out  and evaluated in accordance with  line pipe mechanical test stated in section 3

Hardness testing of repair welds SHALL be in accordance with line pipe mechanical test stated in section 3

  - Cold Expansion.

Submerged arc welding line pipe SHALL normally be cold-expanded for.

The maximum cold expansion is 1.7% measured from unexpanded pipe to expanded pipe.

  - Material

The material used in the manufactured submerged line pipe SHALL be:

- Fully-killed steel.

- Steel SHALL be calcium-treated and preferably vacuum-degassed.

- Weld ability steel for field.

  - Skelp End Welds.

Not applicable

  - heat treatment:

the process SHALL be perform according to documented procedure submitted to the COMPANY for review and approval ,the manufacturer procedure SHALL give details if the pipe as rolled ,normalized ,tempered and quenched   in the quotation.

  - Traceability:

The manufacturer SHALL comply with SR15.1.

Section 3

Line pipe inspection requirements

- line pipe inspection

It is the CONTRACTOR responsibly to provide complete third party inspection to cover the line pipe and coating and all matter relating for testing and quality control according to the following requirements and principals:

  - Chemical tests:

The material and manufactured line pipe chemical testes shall be include but not limited to these described hereafter with responsibility  for checking and inspection of the inspector and contractor.

    - Chemical composition inspection:

The composition of steel pipe used for the manufacture of line pipe furnished SHALL be checked to make satisfaction that the chemical composition is comply with API 5L. Forty second edition –January 2000/table 2B and its foot notes

    - heat analysis inspection:

Certificates of heat analysis SHALL be furnished.

    - Element  analysis inspection:

The pipe manufacturer SHALL furnish a report checked and accepted by the authorized inspection of the product analysis of the furnished line pipe.

Even if these elements are not added on purpose but are present as residuals only.

As minimum each required analysis SHALL be checked by the inspection and SHALL include the following items:

- Carbon, manganese, phosphor, sulphur, chromium, columbium,                                                                                                                                                                                                           copper, molybdenum. Nickel, silicon, vanadium and titanium.

- Any other alloying added a steel making for purpose other than oxidation.

B SHALL not be added on purpose, the maximum percentage SHALL not be Over 0.0005%.

The total percentage of the elements NB+V+TI+CU+MO+CR SHALL not exceed 0.50%.

One pipe per heat of steel SHALL be analyzed. The product analysis SHALL be in accordance with table 2B of API 5L and its footnotes.

The inspection SHALL check the analyzing of this element according to COMPANY requirements per each heat

- Carbon equivalent inspection

The carbon equivalent, based on product analyses and calculations using the Following formula SHALL not exceed 0.43%.

C EQ= C+MN/6 + (CR*+M*+V*) / 5+ (NI*+CU*) / 15

Note:

* If not added on purpose the value found by the heat analysis may be used.

It is the inspection responsibility to check the carbon equivalent per each heat.

  - mechanical tests

The ratio of yield to tensile strength of each test pipe SHALL not exceed 0.85

- Tensile testing inspection

Tensile testing SHALL be carried out on parent metal and weld metal in the stress-relieved condition as indicated on the purchase order, if stress relieving is required for field welding.

      - -longitudinal tensile Test: is not required

      - -transverse tensile test inspection

Transverse tensile properties SHALL be determined on flattened rectangular specimens at the room temperature to determine the yield strength, ultimate tensile stress and elongation.

The tensile requirements (yield strength, tensile stress and elongation) SHALL be checked and accepted by the inspection according to table 3B and its foot notes criteria’s

      - - transverse weld tensile test

Weld tensile specimen SHALL be taken from the same part of the pipe as used for preparing tensile specimens.

The ratio of yield to tensile strength of each test pipe shall not exceed 0.85

      - - Testing Frequency.

There SHALL be at least one tensile test on one pipe per heat of steel, unless one heat is more than 100 tons, in which case at least two pipes per heat SHALL be tested within this requirement the following test SHALL be applied.

      - - control tensile test

Record of such tests SHALL be taken from the plate and SHALL be taken by the manufacturer per heat to be available for checking

      - -elongation

Elongation ‘e’ should be calculated in accordance with footnote of                Table-3B

- bend test:

The specimen SHALL be taken per each heat or less for each wall thickness per each grad  and show no weld repair

The specimen dimensions and jig dimensions SHALL be according to API 1104

The guided bend test SHALL be done for:

          - - face bend test

          - - root bend test

No imperfection with length of more than one and half of the wall thickness in any direction will be accepted.

- fracture toughness testing of line pipe

The fracture toughness of the line pipe SHALL be determined by the manufacturer

  - -Using Charpy V-notch impact test specimens at the -10 C (minus 10 degree centigrade) temperature.

The test SHALL be performed in accordance with ASTM A370.

In each case, three Charpy V-notch specimens SHALL be taken from:

- the base material

- weld centre line

- fusion line

- -the heat-affected zone at 2 mm and 5 mm from the fusion line as shown in Figure 1 below

For all specimens the notch axis SHALL be perpendicular to the pipe surface.

For acceptance, the average reading of the three specimens and the minimum single specimen SHALL comply with the requirement in the following tables.

- For grad X-70

| specimen size mm | transverse |  | longitudinal |  |
| --- | --- | --- | --- | --- |
|  | Average | single | average | single |
| 10X10 10X6.7 10X5 | 48 37 32 | 36 28 24 | 82 64 54 | 61 48 41 |

Figure 1. location of Charpy V -notch specimen

  - Drop -weight tear test

Drop-weight tear tests SHALL be carried out on one pipe of every heat of steel. The tests SHALL be in accordance with SR6 of API Spec 5Lpecification.

- Microstructure and hardness inspection:

During normal production, micro sections and hardness checks SHALL be carried out on one pipe per heat of steel unless one heat is more than 100 tons, in which case at least two pipes per heat SHALL be tested, The micro sections of line pipe SHALL be taken at the weld seam for hardness checks and opposite weld seam for confirmation of effectiveness of shape control.

If specimens or test coupons, for whatever purpose, are taken from the pipe or plate by flame cutting, vendor SHALL, if so required by COMPANY, submit proof that mechanical properties measured have  not  been  affected  by  the heating-up and subsequent cooling, inherent with this cutting method.

Section 4

Hydro test inspection

- hydrostatic tests

  - –for the 36 "

The test pressure for the purchased line pipe SHALL be such that the fiber stress is at least 90% of the specified minimum yield strength calculated on the basis of nominal wall thickness, which SHALL be according to the following table:

| Specified wall thickness |  | The hydro test value |  | Duration |
| --- | --- | --- | --- | --- |
| 0.406 (inch) | 10.3 mm | 1420 PSI | 98 bar | 10 second minimum |
| 0.469 (inch) | 11.9 mm | 1640 PSI | 113 bar |  |
| 0.562 (inch) | 14.3 mm | 1970 PSI | 136 bar |  |

Section 5

Non-destructive inspection

- non-destructive inspection

All non-destructive inspection shall be supervised by an inspector qualified to at least ASNT level II, or equivalent.

Inspection for final acceptance of the pipe by contractor shall be executed after all heat treatment, expansion operations and after hydrostatic testing of the pipe.

Electromagnetic, ultrasonic, radiographic and magnetic particle inspection equipment and procedure SHALL have the prior approval of inspector.

The full circumference of each pipe end after cutting SHALL be tested ultrasonically for lamination over a width of 25mm from the beveled end.

Ultrasonic testing should be carried out  before  and after  beveling,  but  when  done after beveling  it  should be  carried  out  from  the  inside.

Plate ends are not covered by automatic ultrasonic defect testing, manual ultrasonic inspection SHALL be carried out on the pipe ends.

The longitudinal edges of a plate to be used in fabrication of welded pipe SHALL be 100% ultrasonically tested from both sides, over a width of at least 25mm of the trimmed plate width.

In addition to edge testing, checks SHALL also be made over the remainder of the surface as follows:

Lamination testing of each plate, rolled from ingot or continuous cast material, should be along a sinusoidal or zigzag pattern, which may be carried out on pipes by rotary ultrasonic testing.

If not possible then the scanning SHALL be along parallel lines selectively distributed to give good coverage, with a greater amount of checking in the center. In either case at least 25% of the plate surface SHALL be covered.

- -radiolographial inspection

- Scope.

The complete length of the weld seam SHALL be radiographic tested

- Equipments.

The radiographic examination SHALL be executed with X-ray equipment, using fine-grain film, e.g., Gevaert-Type D7 or equivalent, and lead intensifying screens.

For acceptance of the radiographic films, the equipment and technique used SHALL result in sensitivity better than 2% of weld metal thickness and in a relative film density of 2.5 to 3.5 in weld metal. The technique used SHALL be qualified by the vendor and approved by inspector.

- Reference Standards.

The penetrameter used SHALL be of the wire type in accordance with IIW/IIS 62-60. An equivalent penetrameter may be used if approved by   COMPANY. A penetrameter sensitivity of better than 2% of weld metal thickness SHALL be achieved, the penetrameter being placed across the weld on the same side as the radiation source. If this is not possible then, provided that the technique has been proven to achieve a sensitivity of better than 2%, the penetrameter may be placed on the film side but a lead letter "F" must be used to indicate that the placing is source side.

- Imperfections.

Gas pockets with a diameter of 3 mm and larger are not acceptable, nor are worm holes with a visible length on the radiographic film of 3 mm or more.

- Weld Repair.

- Repairs are not acceptable in the welds within a length of 200 mm from the pipe ends.

- -Ultrasonic And Electromagnetic Inspection

- Scope

- The end of pipe and end cutting which not covered by radiographic SHALL be ultrasonic inspected

- Equipment.

The ultrasonic equipment SHALL incorporate:

A device which monitors the effectiveness of the coupling, i.e. loss of coupling exists when it is less than -6 dB, referred to the static calibration.

An audible warning system and a painting spray system (or equivalent) operating when the coupling is unsatisfactory.

An automatic paint-marking device (or equivalent) activated when the ultrasonic echo received exceeds the pre-set acceptance limits.

This alarm should react on all inspection and control functions within 1 mm and the reset time on the monitors SHALL be such that, after detection of a defect the alarm system will again be available for detection within 25 mm advancement in the scanning direction.

An automatic guiding device for correct positioning of the crystal probes with respect to the weld centre.

Transducers, which are accommodated to the wall thickness and, if applicable, the weld preparation.

Probe entrance angles should be as follows:-60-70   degrees

For a 100% volume defect inspection, the transducer arrangement SHALL be such that it results in a sound intensity, referred to the maximum sound intensity found in the static calibration that exceeds 6 DB at any point in the pipe wall in the longitudinal direction.

- The sound intensity in the circumferential direction should exceed

- 2 DB.

The probe(s) used for the wall thickness/lamination check SHALL satisfy the following requirements:

For twin crystal probe(s): the focal length SHALL be approximately 50% of the wall thickness at recording level.

Reference target for lamination check: the echo of a 6.3 mm diameter flat bottomed hole at mid-wall position is the recording level.

- Reference Standards.

3.2 mm hole SHALL be used for sensitivity calibration.

- Acceptance Limits

    - The acceptance limit signal for pipe is 100%.

    - If continuous signals occur which are outside the acceptance limits, in areas where upon subsequent investigation no defects are detected, further investigation using other methods SHALL be executed to establish the cause.

    - For all pipe ends and for the plate laminations are acceptable if either the dimension along the minor axis of the lamination does not exceed 6.3 mm, or the product of the dimensions along the major and minor axes does not exceed 50 mm2.

- Very important note

- The residual magnetic field created by ultra sonic or electro magnetic scanning device shall be released and such residual magnanimity shall be inspected and accepted by inspector

- -Magnetic Particle Inspection of Beveled Surfaces.

  - Scope

After beveling the pipe ends, the bevel surface SHALL be subjected to wet magnetic particle inspection, in accordance with BS 6072, using materials in accordance with BS 4069, or equivalent standards.

  - Acceptance Limits for Beveled Surfaces.

The beveled surface SHALL be free from defects visible to the naked eye such as laps, cracks or laminations.

- Section 6

- Workmanship, visual inspection and defect repair

- workmanship ,visual inspection and defect repair

Every 24",36" line pipe SHALL be examined internally and externally for surface faults in the welds and in the body of the pipe.

Every 16" line pipe SHALL be examined externally for surface faults in the welds and in the body of the pipe.

For internal examination inspector SHALL pass through the bore of the pipe. Therefore adequate illumination SHALL be provided to facilitate proper examination.

If inspector has to reject pipe repeatedly for any re-occurring cause, this SHALL be sufficient reason to refuse further pipes for final examination until the cause has been corrected.

In the event that defective plates, pipe or welds are detected during additional investigations by COMPANY, CONTRACTOR and COMPANY SHALL mutually agree on additional inspection requirements.

The cost of such additional inspection SHALL then be borne by CONTRACTOR.

- Workmanship.

- Dents

All cold-formed dents with a sharp bottom gouge and all sharp gouges (without dents) deeper than 0.8 mm SHALL be considered injurious.

- Offset of Plate Edges

The maximum allowable misalignment SHALL be 10% of the wall thickness or 1.5 mm, whichever is the smaller.

- Height of Outside and Inside Weld Beads.

At pipe ends and other areas which are radio graphed, the excess height, i.e. reinforcement of both the inside and the outside bead, SHALL allow adequate interpretation of radiographs at centre and sides of welds.

- Hard Spots

Hardness greater than 22 HRC (250 HV) is rejectable.

- Defects.

Injurious defects may be removed by grinding, provided that the wall thickness remaining is not below the specified wall thickness less the minus Tolerance.

In all cases where grinding repairs are made as a result of imperfections disclosed by non-destructive testing, the part  of the pipe containing such repairs SHALL be given an Additional   non-destructive   test   after   the grinding operation at no cost impact to the COMPANY.

- Repair of Defects.

    - Repair in the weld seam is not acceptable within 200 mm from the bevel end.

    - Repair welding of cracks is not allowed.

    - Weld repair of arc burns is not acceptable.

    - If defects are found in the weld seam, which are unacceptable by ultrasonic testing, a radiograph SHALL be made to assist in the interpretation of the type of defect, before any repair is carried out.

    - Repair welding SHALL only be executed after specific approval of each proposed repair by inspector.

    - Repairs to the weld seam  SHALL be limited to three per pipe.

    - The total length of repair welding SHALL not exceed 5% of the total weld length in each pipe.

    - The repair of pipes with defects in excess of these limits SHALL   only be permitted with the prior approval of COMPANY.

Welding repairs shall not be carried out on a pipe weld after it has been cold-expanded or hydrostatically tested.

Section 7

Line pipe dimensions and tolerance

- line pipe dimensions and tolerance

- length

Pipe SHALL be supplied in the following lengths:

95% minimum from each group of wall thickness, between 11 and 12 m

No length SHALL be less than 8 m

- Wall Thickness

The wall thickness at any point in the pipe at final inspection SHALL not deviate from the nominal thickness by more than +10% or -5%

Important note

The maximum acceptable minus tolerance shall not exceed 5%

In removing the inside burr at the pipe ends, care shall be taken not to remove excess metal and form an inside bevel.

Removal of excess metal beyond the minimum wall thickness as indicated in the table above SHALL be cause for re-beveling.

- line pipe tolerances

The accepted tolerances in accordance API 5L except the wall thickness tolerance

Section 8

First day manufacturing testing

- first day manufacturing tests

- Approval by the COMPANY notwithstanding, of the manufacturing and procedure test in accordance with this specification, four of the completely finished pipes of the first-day production, two from each of the first two heats, except where specified otherwise in this section, SHALL be selected at random for testing to verify that the Submitted manufacturing procedure results in fully acceptable pipe.

- At the COMPANY's option, a specialist appointed by the COMPANY may make the selection.

The pipes tested as above SHALL be considered to be the test pipe(s) per heat or per shift as required in this specification.

First-day Production test SHALL be repeated upon any change in the manufacturing procedure or interruption to the program.

CONTRACTOR SHALL submit to COMPANY a report giving the results of all tests indicated below together with the macrostructure of the plate and seamless pipe.

The report SHALL be agreed and countersigned by the specialist referred to above.

These pipes SHALL be tested in accordance with the following amended by this specification.

- Visual Examination

All pipes SHALL be examined visually for dimensional tolerances, and for surface defects in the dimensions (out side diameter, wall thick ness) and workman ship described in section 6and 7

- Ultrasonic Examinations

The weld seams of all pipes SHALL be examined by means of an automatic ultrasonic scanning device in accordance with clause 5.2 of Section 5.

- Radiographic Examination

The welded seams of all pipes SHALL be radio graphically examined throughout their full length in accordance with clauses 5.1 of section5

- Dye Check or Magnetic Particle Test

The weld seams of all pipes SHALL be subjected to dye check or magnetic particle inspection throughout their full length in order to check on longitudinal and transverse surface defects in the weld material.

Dye check materials and checking procedure SHALL have prior approval of inspector. Cracks are unacceptable; if found their cause SHALL be investigated.

- Mechanical Testing

The mechanical properties of all pipes SHALL be tested as specified below.

Test results SHALL meet the requirements for specified grade and type of pipe.

      - Weld Seam

The weld seam of all selected welded pipes SHALL be mechanically tested as required in Section 3 of this specification.

In addition an all-weld metal tensile test SHALL be made, including the determination of tensile strength, yield strength and elongation.

Results of the all-weld metal tensile tests SHALL meet the minimum specified requirements of the plate from which the pipe is made.

Weld impact tests SHALL be made in accordance with Supplementary Requirement SR5 API 5L .

      - Pipe Material

Mechanical tests SHALL be carried out on or on two pipes made from different heats, as required by Section 3 of this specification.

      - Impact (Fracture Toughness) Test

- Charpy impact test

- Drop-weight tear test

      - Macrographic, Micrographic and Hardness Examination

Three specimens from one pipe SHALL be extracted from locations to be chosen by inspector across the weld.

These specimens SHALL be cross-sectioned, polished and etched for macro-examination.

This examination SHALL provide evidence that proper fusion has been obtained throughout the full thickness of the joint, particularly as affected by the depth of penetration of inside and outside welds, their degree of alignment and interfusion.

A series of Vickers hardness readings (30 or 10 kg load) SHALL be made on one of the above etched specimens selected by inspector.

These series of readings SHALL extend from unaffected base metal on one side across the weld to unaffected base metal on the other side.

Three traverses SHALL be made, one 2 mm in from the outer edge, the second across the centre and the third 2 mm in from the inner edge.

Readings SHALL be about 1 mm apart.

no hardness value SHALL exceed 250 HV in any cases

Section 9

Coating application and requirements

- coating

- Scope:

  - This specification covers the minimum requirement of the COMPANY for the application and testing of factory applied polyethylene coating for line pipe.

  - Within the following contract data the contract SHALL apply line pipe coating:

- The maximum operating temperature of the pipeline is 52 degree centigrade

- The project in almost cross desert land include many wadis

- Expected ambient temperatures during installation is 52 degree centigrade

- Expected black bulb temperature during installation 82 degree centigrade

- The coating SHALL three layers

  - This specification covers the requirement and test methods for factory applied external polyethylene coating of bare steel pipes, applying one of the following processes:

- Circular or cross-head extrusion.

- Side extrusion.

- Surface preparation:

  - Surface cleaning:

Immediately prior to blast-cleaning, the pipes SHALL be inspected for surface contamination.

All grease, oil or other surface contaminants SHALL be removed by a suitable solvent.

Pipes which have been subjected to salt spry SHALL be washed prior to blast - cleaning with fresh, potable water ensuring that the contamination is not spread over the surface if chemical cleaner is used, subsequent washing with potable water will be necessary. The pipe surface SHALL be dried before blast-cleaning.

The grade of surface finish after blast-cleaning SHALL be in accordance with SA 2 ½. The surface profile after blast-cleaning SHALL have a peak- to -trough height between 0.050 mm and 0.1mm and SHALL be measured by a method agreed with the COMPANY.

Directly before coating, any dust, grit or other contaminants SHALL be removed from the pipe surface by a method to be advised by the Applicator and approved by the COMPANY.

Where rust blooming or further contamination has occurred, the pipe surface SHALL be blast-cleaned again. Coating SHALL take place before any contamination or rust blooming appears.

Blast-cleaning SHALL be suspended when the pipe surface temperature falls to within 3 degrees c of the dew point, or is less than 10 degrees c.

  - Surface inspection prior to coating :

The metal surface SHALL be inspected immediately after blast- cleaning by the Applicator under adequate lighting, and all silvers, scabs, gauges etc. Made visible SHALL be removed by grinding within the limits allowed by the applicable line pipe specification.

The Applicator SHALL not make any other repairs unless explicitly permitted by the applicable line pipe specification.

Any repaired areas SHALL be blast-cleaned to meet the requirements of 9.2.1 above.

- Coating application requirements:

The Applicator SHALL coat the pipe in accordance with the following, using one of the Processes mentioned in 9.1 above.

The frequency of use of the batches of polymer SHALL be in the order in which it has been manufactured.

For all processes, the preheating temperature of the pipe SHALL comply with the procedure approved by the COMPANY.

The heating equipment SHALL be suitably controlled to maintain uniform temperature and to achieve the required uniform temperature along the total length of the pipe joint.

Prior to coating, the pipe temperature SHALL be checked with approved and calibrated instruments to ensure that the temperature complies with the established coating procedure.

- Coating layer requirements:

  - General:

The coating layer requirements SHALL be demonstrated by the Applicator by means of single test for each composition of plastic material and for each application process adopted. Recent tests witnessed by an independent certification agency may be accepted by COMPANY.

The first coat shall be epoxy primer layer

The second coat is adhesion layer

The third coat shall be 950kg/m3 density polyethylene layer

These three layers shall be suitable for desert area and high temperature black bulb temperature and rocky lands

  - Coating layer thickness:

The coating layers SHALL have a minimum thickness of 3 mm   PE- coating.

The coating thickness SHALL be measured using a thickness meter based on Eddy Current or electromagnetic techniques or equivalent in accordance with ISO 2808, method 6A or 6B.

Magnetic thickness gauges SHALL not be used, either for qualification testing or for quality control purposes.

The thickness gauge SHALL be calibrated at least once per shift. Calibration SHALL be carried out on a steel plate of similar thickness as the pipe wall using plastic shims of the same thickness as the nominal coating system.

For quality control purposes a minimum of twelve thickness checks SHALL be made at approximately one quarter, one half and three quarters of the length of each pipe and at the 3, 6, 9 and 12 o'clock positions around the pipe. For submerged arc welded pipe one of these circumferential positions SHALL be on top of the weld.

  - Polyethylene density:

The density of polyethylene shall be 950 kg/m3

  - Holiday detection:

The coating SHALL be free from holidays when tested in accordance with 9.7.3

  - Adhesion:

The adhesion of the coating in the transverse and in the longitudinal direction SHALL be at least 3.5 kg/cm at 20 degrees c, and 2 kg/cm at 50 degrees c when tested in accordance with (9.7.4). Spring balance method SHALL be allowed.

  - Appearance:

The coating SHALL be free from blisters, pinholes, scratches or any other irregularities and SHALL have uniform colour, gloss and thickness.

- Pipe end:

The ends of pipe SHALL be bare over a length of 140 mm  10 mm.

The coating SHALL be chamfered by suitable practice to an angle of 15 or 45 degrees. The bare ends, including the transition zone SHALL be painted with a removable varnish as a temporary protection against corrosion during as portation.

The varnish SHALL be shown to COMPANY’s satisfaction to be easily removable by Power brushing and by shot blasting.

- Inspection and testing procedure :

  - General:

The COMPANY SHALL have unrestricted access to all departments of the coating yard when coating of the pipe or testing of the material is executed.

In the event that problems are detected or repairs are needed, the Applicator SHALL take immediate steps to correct the situation to the satisfaction of the COMPANY.

  - Quality control of pipe coating:

The Applicator’s quality control department SHALL be responsible for timely warning, and the Applicator’s production department for timely correction of problems and repair of equipment to avoid any serious delay in the production.

They SHALL communicate with the COMPANY and arrange for checks as described under 9.7

Records SHALL be kept of pipe coated by the Applicator and SHALL be made available as requested by the Inspector and these records SHALL show:

- The Applicators number for each pipe.

- Pipe mill serial number and heat number for each pipe.

- Number of pipes rejected per shift and cause of rejection.

- Date and time on which a new batch of polymer is fed into the coating application plant.

- Maximum temperature to which pipe joint has been subjected

After coating, the pipe manufacturer’s information (painted on the inside of the pipe) SHALL be stencilled on the coated surface with lettering.

- Inspection and testing requirements :

Inspection SHALL include, but not limited to, monitoring of the surface cleanliness, measuring of the surface profile and coating thickness, holiday detection, adhesion testing and visual inspection.

The frequency of testing where not specifically indicated SHALL be agreed between the Applicator and the COMPANY.

The tests described hereafter SHALL be witnessed by the Inspector.

    - Surface profile:

The surface profile SHALL be measured in accordance with a procedure agreed with the COMPANY. The meter SHALL be calibrated daily.

The frequency of testing SHALL be 2 pipes per shift.

    - Coating thickness:

The method for measurement of the coating thickness SHALL be approved by the COMPANY.

The measurement equipment SHALL be calibrated at least once per shift.

A minimum of twelve thickness checks SHALL be made at three equidistant locations spread over the total length of the selected pipe joint at the 3, 6, 9, and 12 o’ clock position around the pipe four (4) positions SHALL be over the weld.

Initially one out of ten pipes SHALL be selected for coating thickness checks.

The frequency may subsequently be varied, based on the quality history and with the agreement of the Inspector.

    - Holiday detection:

Every pipe SHALL be inspected for holidays over 100% of its coated surface with a holiday detector approved by the COMPANY.

The coating SHALL be checked with the holiday detector after the coating has cooled to at least 100 Deg c0 or such other temperature approved by the COMPANY.

Holiday detection SHALL be carried out only on moisture - free surfaces.

The Applicator SHALL demonstrate to the Inspector that the setting of the detector is satisfactory for detecting pinholes. This setting SHALL be checked once every two hours with a voltmeter.

Every coated pipe with more than two holidays SHALL be rejected and subsequently stripped and recoated. In this case, the coating process SHALL be checked to determine the cause of the High Holiday rate.

If the cause is not resolved after two consecutive pipes, the coating process SHALL be stopped for full investigation.

Coated pipes with not more than two holidays SHALL be repaired in accordance with a procedure approved by the COMPANY.

    - Adhesion test:

The adhesion of the coating in the transverse direction at ambient temperature SHALL be checked on one pipe per shift selected at random.

In addition, the Applicator SHALL check the adhesive strength at 50 day by performing one test on a first-day-production pipe.

An adhesion test at ambient temperature SHALL also be carried out in the longitudinal direction

The result SHALL be recorded and reported. These tests SHALL be carried out on a minimum of one pipe per day of production.

Spring balance method SHALL be allowed.

    - Appearance:

Every pipe SHALL be visually inspected for compliance with requirements of this specification stated in 9.4.5 above.

- Coating layer requirements:

The Applicator SHALL carry out repairs to the coated pipe at no expense to the COMPANY.

Scars, dents, damaged areas and holidays SHALL be cleaned by removing all rust, scale, dirt or other foreign matter or loose coating using a small file.

Repairs are to be made by means of a repair procedure to be submitted to and approved by the COMPANY prior to the start of the work. Any repair to the coating SHALL have the approval of the COMPANY. Any pipe subject to a coating repair procedure SHALL be fully re-examined in accordance with the requirements 9.6 and 9.7

- Handling, storage and transport of bare and coated pipe:

The pipe manufacturer SHALL be fully responsible for the overall coordination and delivery of the pipes to the coating Applicator.

The coating Applicator SHALL furnish all equipment, plant space, stockpile areas, labour supervision and materials to perform the following activities:

- The receiving of bare pipe to be laid down by the pipe manufacturer at the coating Applicator’s yards or at such other location which may be mutually agreed by the coating Applicator and the pipe manufacturer.

- The stockpiling of bare pipe.

- The application, testing an inspection of the pipe external coating.

- The repair of coating of all tested pipes which are rejected, And repair of sample pipes which are deliberately damaged during testing (e.g. peel test) at the coating Applicator’s expense.

The rejected pipe may require removal of all coating and then recoating if, in the opinion of the Inspector, this is the only way in which the coating can meet the specification.

- The repair of all damaged coated pipe prior to shipment from the coating Applicator’s yard.

- The stockpiling of coated pipe in the coating Applicator’s storage areas.

- The preparation of the coated pipe for transport and transfer to transport facilities for shipment.

The Applicator taking delivery of the bare pipes SHALL unload them using slings, spreader bars, protected hooks, etc.

Approved by the COMPANY, so as to prevent the pipes from being damaged.

When taking delivery of the bare pipes the Applicator’s SHALL inspect each pipe for damaged. All visible defects SHALL be reported to the COMPANY.

Damaged to the pipes occurring after the Applicator has taken delivery of the pipes, such as dents, flats, or damage to bevels, SHALL be cut off or removed and the pipe SHALL be rebevelled. This work SHALL be carried out subject to approval by the COMPANY. The cost of this work, as well as that of the pipe lost as a result of the repair, SHALL be for the Applicator’s account. Any repaired pipe is subject to COMPANY’s acceptance criteria as applied in the pipe mill.

The Applicator SHALL ensure that stacking of the uncoated pipe is done such that no ovalling at pipe, flattening or any other damage to the pipe can occur due to e.g. the weight of the pipe or too widely spaced supports.

Care SHALL be taken to prevent damage to the coated pipe. It SHALL be handled using spreader bars, slings and hooks lined with soft rubber or plastic. Rubber aprons SHALL be attached to End hooks for the purpose of protecting pipe ends unless they are provided with adequate and protectors. Direct metal to coated pipe contact SHALL be avoided during lifting.

The coating pipes SHALL at all times be stored completely clear of the ground. For storage purposes the coated pipes may be laid on wood with a suitable covering (foam rubber) or on pipes of stone-free sand.

The pipes may be stacked only to such a height as to ensure that no flattening and damage to the coating or pipe can occur through the width of the pipes or too widely spaced supports.

Throughout the storage period the Applicator SHALL bear full responsibility for the coating. Damage or flattening of the coating SHALL be corrected by the Applicator at his own expense and to the satisfaction of the COMPANY.

Coated pipe may under no circumstances be dragged or rolled over the ground.

During transport the pipes SHALL be stacked and secured such that they cannot be damaged (e.g. by abrasion).

The following standards SHALL be taken into Consideration, and adhered to if they are more stringent or restrictive than the pipe manufacturer’s procedures:API RP 5L1.

Pipe damaged in transit and during on / off loading between pipe manufacturer’s yard and coating yard SHALL be Repaired or replaced by the pipe manufacturer. Pipe or coating damaged in the coating Applicator’s premises prior to shipment SHALL be repaired by the pipe manufacturer and/or the coating Applicator. Pipe and coating damaged prior to hand over to the COMPANY at the point of delivery SHALL be repaired by and at expense of the pipe manufacturer and/or the coating Applicator.

Section 10

Marking

- marking

- scope of marking

In addition to the marking of pipes, CONTRACTOR SHALL supply to COMPANY, lists of pipe produced stating pipe identification numbers, heat numbers, and dimensions, weights of lots or of pipes, purchase order numbers, type of certificates issued, and any further items that may be indicated on the purchase order.

The CONTRACTOR marking SHALL be executed on the external coating surface and the internal pipe surface with white block capitals of minimum height 25 mm and such marking SHALL show the following as minimum:

- The manufacturer API license number.

- API monogram and date

- The pipe number and heat number.

- The pipe dimensions (the out side diameter , wall thickness, length and pipe weight)

- The grad of pipe

- The line pipe product specification level.

- The process of manufacturing

- The applied heat treatment.

- The test pressure

Marking of test pressure, sizes (diameter and wall thickness) and weights SHALL be in metric units.

Cold die stamping is not permitted on the pipe body or on the weld.

When pipe has been inspected/tested by an inspection agency, or testing by vendor has been witnessed by an inspection agency, the agency representative SHALL stamp the bevel of each pipe next to the identity number.

Section 11

Line pipe handling and shipping

- line pipe handling and shipping

- scope

All pipe SHALL be handled, loaded and shipped in accordance with API RP 5L1,

CONTRACTOR SHALL submit loading instructions and diagrams for approval for all pipe shipped by truck or vessel; however, approval of these SHALL not relieve CONTRACTOR of his Responsibility for any damage during shipment.

- Lifting

The pipe SHALL be handled in such a manner that it does not strike objects which may damage the pipe and/or coating.

Pipe SHALL be lifted, moved and lowered from one position to another by suitable and certified equipment.

When lifting pipe, non-abrasive wide nylon pipe slings or special lifting hooks equipped with a non-metallic bevel protector, such as Teflon inserts, SHALL be used.

Pipe hooks SHALL be curved to fit ID of pipe. Furthermore, when windy conditions prevail, a tug line SHALL be used to prevent pipe from swinging.

Temporary attachments for handling or lifting SHALL not be welded to any pipe.

Pipe bevel protectors removed for handling SHALL be replaced to prevent ingress of dirt and sand.

- Transport

Trucks used to transport coated pipes SHALL have an uninterrupted flat bed of approximately 12 metres length and 2.4 metres. Width equipped with side stanchions of about 0.9 m height. Pipes SHALL be protected against truck bed by means of at least five nonmetallic cross beams. Non-metallic separation SHALL be provided to avoid any damage to coating by side stanchions.

After loading, suitable non-metallic slings SHALL be used to tie the load securely to the truck. During transport the tension of these slings SHALL be regularly checked. Pipe ends SHALL be protected from contact with other metallic materials.

CONTRACTOR SHALL ensure that no bevel protectors can be lost during transport.

Special marine transportation shall be considered during transportation in accordance with PR5L W

- Storage

pipes SHALL be stacked using rubber or other suitable separator strips (e.g. PE ropes)

CONTRACTOR SHALL verify with COMPANY the acceptable stacking height for line pipe in storage.