10-CATHODIC PROTECTION scope

10.1	GENERAL DESCRIPTION

10.2	MATERIALS

10.3	MATERIAL ACCEPTANCE PROCEDURE

10.4	CATHODIC PROTECTION MATERIALS INSTALLATION PROCEDURE

10.5	CATHODIC PROTECTION SYSTEM INSTALLATION

10.6	CATHODIC PROTECTION SYSTEM COMMISSIONING

10.7	CATHODIC PROTECTION DRAWINGS

10-CATHODIC PROTECTION

10.1	GENERAL

In addition to this specification refer to Specifications occurring in the Al Furat Petroleum Company Schedules "CP-PL" and "FF", The British Standard BS-3900, the IEE Standard for Underground Cables, ASTM Cable Standards and appropriate NACE Standards. The most stringent specification, for a particular material from the above sources, takes precedent over all others.

10.2	MATERIALS

10.2.1	Rectifiers

#### General

-	The rectifier units shall be approved by the Syrian Gas Company prior to manufacturing or shipping.

-	All rectifier components shall be warranted to be free from defects in design, material and workmanship, for a period of one (1) year after date of delivery.

-	The rectifier shall be oil cooled and be capable of operating continuously at the full rated output in an ambient temperature of 52o C with a minimum expected life of 20 years.

-	DC output from each rectifier shall be as per the appropriate drawing.

-	AC input to the rectifier shall be 220 volts, 50 Hz, single phase with a maximum current draw of 5 amperes.

10.2.1.1	Transformer

-	The transformer shall be designed as full isolation with separate and isolated primary and secondary windings.

-	The transformer shall be designed to operate at 50 Hz.

-	Continuous over voltage:  Transformers shall withstand continuous operation with input voltage rises of 10% above rating after the rectifier has been set to operate at maximum rated DC voltage and amperage.

-	Temperature rating:  Transformers shall be designed for a maximum hot spot heat rise of 65o C (actual temperature 110o C in 45o C ambient).  All insulation shall meet AIEE requirements for Class 'B' (130o C) operation or above.

-	Dielectric Strength:  A minimum of 2250 volts applied for one minute between windings and windings and core.

-	Transformer Cores:  Cores shall be constructed of grain-oriented silicon steel, gauge 26 or lighter.  Core losses shall be less than 1.5 watts per kilogram.

-	Transformer Efficiency:  Shall not be less than 95% and the power factor not less than 95% when operating at full rated output.

-	Voltage Regulation:  Voltage regulation shall be no more than 3% at rated load from no load.

10.2.1.2	Rectifying Element

The rectifying element shall be a full wave bridge and be composed of either silicon diodes or a selenium stack.  The rectifying element will be derated to 50% of the manufacturer's published rating at an operating temperature of 100o C.  In addition, to allow an adequate margin for over voltage and current surges, the cells shall be protected by metal-oxide Varistors and by current-limiting fuses.  Heat sinks of copper or aluminium shall be sized to keep the junction temperature well below the maximum recommended by the manufacturer.

10.2.1.3	Circuit Breaker

Circuit breakers shall be of the manually reset type, 100% magnetic and be unaffected by changes in ambient temperatures.  Single pole breakers shall be used for 115-volt, single phase AC input.  Double pole breakers shall be used for all other single phase input voltages.  Three pole breakers shall be used for all three phase input voltages.  The breakers shall be sized to hold 100% of the rated load and trip between 101% and 125% of the load.

      - Fuses

The DC output of the rectifier shall be equipped with rectifier fuses to protect against overload and short circuits.  The fuses shall be sized for 105% to 140% of the rectifier rated current output.

10.2.1.5	Meters

The DC voltage and current output meters of the rectifier shall have an accuracy of 2% at 25o C with a temperature stability of 0.5% per 5o C.  The meter scale shall be sufficiently large to easily distinguish 0.5 volt and 0.5 ampere increments.  Also, the meters shall be marked at the rated DC outputs and these shall fall within 70% to 90% of the full meter scale.  An external shunt for the ammeter shall be provided for the negative circuit.  Individual ammeters and voltmeters shall be used.  The shunt shall be rated for a 50 millivolt voltage drop at the full scale current rating of the ammeter.

10.2.1.6	Terminals & Contacts

-	All current carrying mechanical contacts shall be composed of nickel-plated brass or copper and be tightly secured with lock washers or other positive locking devices.

-	All brass and copper conducting elements shall be conservatively sized for the current carried at full rated rectifier output.

-	All mechanical contacts must operate at less than half (1/2) of the maximum current rating specified by the manufacturer for other industrial uses.

-	An accurate wiring diagram designating all components shall be provided with each rectifier unit.

-	DC terminals shall be located in the instrument compartment described further on in these specifications.  The DC connections shall be pressure type terminals of nickel-plated copper or brass.  Wire sizes accommodated shall be in accordance with the following table:

Rectifier DC Rating			Terminal Lug Size

Up to 30 Amperes			#8 to #2 AWG (8.37 mm2 - 33.6 mm2)

30 Amperes and Over			#4 to #2/0 AWG (21.1 mm2 - 67.4 mm2)

Lugs to be clearly labelled positive and negative.

AC terminals shall be insulated to withstand 8000 volts to the enclosure with shielding provided to prevent accidental contact.  The AC terminal size shall be adequate to accommodate #6 AWG (13.3 mm2) wire at rated input currents up to 25 amperes and #4 AWG (21.1 mm2) wire at higher input current ratings.  Connection instructions for input leads shall be clearly visible near the input terminals.

10.2.1.7	Lightning and Surge Protection

Lightning arrestors shall be installed on both the AC and DC side of the rectifier units.  The rectifier bridge shall also be protected from surges by metal-oxide Varistors.  The arrestors shall be fast acting spark gap or silicon oxide Varistors and able to withstand a minimum of 500 Joules on the DC side and 1000 Joules on the AC side.  The arrestors shall not be placed in the oil compartment.

10.2.1.8	Efficiency Filter

All units shall be supplied with a capacitive filter or inductive choke to improve rectifier performance and ensure true DC output.

10.2.1.9	Rectifier Enclosure

-	All cases shall meet the latest N.E.M.A. standard for electrical enclosures or shall be of stainless steel sheets.

-	The rectifier shall be sheet steel having a minimum thickness of 12 gauge back, top, sides and front and shall be finished inside and out with 3-5 mils fusion bonded polyester powder coating or equivalent coating. The coating must be able to withstand 82oC in direct sunlight, for a period of 20 years.  The colour shall be light grey.

-	The case shall be designed to withstand a constant 0.5 psi positive or negative pressure and an instantaneous pressure of 5 psi.

-	The rectifier enclosure shall be sized for 4 sq. in. per watt of dissipated heat operating at 100% of rated DC output.

-	The rectifier shall have a removable chassis containing the rectifier elements immersed in oil.

-	All instruments, alarm boards, AC breakers, DC fuses, shunts, current interrupters and DC cable lugs shall be housed in a separate cabinet outside of the oil filled compartment.  This cabinet shall also meet N.E.M.A. standards and be coated exactly as the main rectifier compartment.  The instrument cabinet shall be weather and dust sealed.

-	Each unit shall be supplied with a sun guard to shade the rectifier and provide an amount of protection against rain, snow and dust.

-	A 1" and a 2" knockout for AC and DC conduits shall be provided on the rectifier case.

-	If AC or DC cables connect below the oil level, copper bars of sufficient size shall be extended 2 inches vertically out of the oil to prevent oil wicking.

10.2.1.10	Transformer Oil

-	Must be free of acids, alkalis, and corrosive sulphur.

-	Must not attack varnish finishes on transformer windings, etc.

-	Must not contain PCB's (polychlorinated biphenyl).

-	Must have a flash point above 125 oC.

-	Must not readily form sludge or water emulsions.

-	Must have a volume resistivity exceeding 1 x 1010 ohms-cm.

10.2.1.11	Miscellaneous

-	Each rectifier shall be equipped with an alarm board capable of running a relay on the DCS System.  The alarm should activate on no DC voltage or amperage, high voltage or amperage, or low amperage.

-	Current Interrupter - Either an attached, self timing current interrupter, adjustable from 1-40 seconds "On" and 1-20 seconds "Off" and synchronizable with a master clock or portable synchronizable interrupters shall be provided with each unit.

-	The following data is to be permanently attached to the rectifier:

-	Manufacturer

-	Model Number

-	Serial Number

-	AC Input Volts - AC Input Amperes

-	AC Line Frequency

-	Number of Phases

-	DC Output Volts

-	DC Output Amperes

-	Ambient Temperature Rating

-	In the case of selenium stacks the following minimum information shall be designated on the rectifier stack:

-	Type of circuit

-	Number of cells in series in each bridge arm.

-	Cell dimensions

-	Alternating current inverse voltage rating of the cell

-	Spacing between cells

-	Number of cells in parallel in each bridge arm.

-	Mounting

-	Finish

-	Manufacturer

-	Identification Tags - Stainless Steel or aluminium tags shall be provided with each unit and carry the unit identification number.

10.2.2	Anodes

10.2.2.1	General

-	The anode lead cable shall be #8 AWG (8.37 mm2) stranded annealed copper wire insulated with a jacket of polyvinylidene (PVDF) and high molecular weight polyethylene or PVDF and modified polyolefin.  The total insulation thickness shall be at least 2.1 mm.  The polyethylene shall conform to ASTM D-1248, Type I, Class C, Category 5.

-	The lead cable shall be connected to the anode in accordance with the anode manufacturer's specifications.

-	The anode to lead connection strength shall exceed the minimum breaking strength of the connecting cable.

-	Anode lead lengths are provided on the Material List.

10.2.2.2	Cast Iron Anodes

-	All anodes shall be centre-connected, tubular design having the minimum dimensions of 56 mm x 2133 mm and a minimum weight of 46 lbs. (20.9 kg).

-	All cast iron anodes shall be of the high silicon-chromium type meeting the ASTM A-518, Grade 3 standard with a nominal chemical composition as follows:

Silicon		-	14.2 % to 14.75%

Manganese		-	1.50 % max.

Carbon		-	0.75 % to 1.15 %

Chromium		-	3.25 % to 5.00 %

Molybdenum		-	0.2 % to Max.

Iron			-	Balance

-	The anode castings shall be metallurgical uniform and free of excessive porosity.

-	The anode to lead connection shall be made in accordance to the anode manufacturer's specifications.  The connection shall be sealed appropriately.

10.2.2.3	DC Cable

-	Only two DC cables shall connect to the rectifier.

Positive Cable

-	All positive cables shall be composed of a stranded soft annealed copper conductor insulated with high molecular weight polyethylene.  Insulation shall comply with ASTM D1248, Type I, Class C, Category 5.  The colour shall be black unless otherwise specified.

-	Minimum insulation thickness shall be 2.78 mm.

-	Buried sections of positive cable, from the rectifier to the ground bed, shall be free of splices.

-	The size of the conductor shall be as per the Bill of Materials and Cable Schedule.

Negative Cable

-	All buried negative cables, expect armoured cables, shall be stranded soft annealed copper conductor coated with high molecular weight polyethylene insulation.  The colour shall be white unless otherwise specified.

-	As with the positive cable, the negative cables shall be splice free from the rectifier or negative splitter panel to the structure connection.

-	The size of the conductor shall be as per the Bill of Materials and the Cable Schedule.

Armoured Cable

-	All single and multiple conductor armoured cables shall have an external HMWPE coating over the armouring.

-	The cables must meet the requirements for placement and operation in a Class I, Division II hazardous area.

-	Any cable splice junctions occurring in a Class I, Division II hazardous area must be made inside of an explosion proof junction box and be sealed appropriately.

-	The conductor size must be as per the cable schedule.

10.2.2.4	Cable Connections to Structures

All negative cables, bond cables, test lead cables, interference control panel cables, etc. shall be terminated to an underground flowlines utilising stainless steel banding, clamps or termite welding.  All above ground negative connections and bond connections shall utilise termite welding.  Termite charges are not to exceed 15 gm.

10.2.2.5	Ground bed Backfill

Impressed current anodes shall be back-filled with calcined petroleum or metallurgical coke breeze having the following chemical and physical properties:

Chemical Analysis					Physical Analysis

Moisture		0.55% Maximum		Bulk Density:  1024 kg/m3

Volatiles		1.0%	Maximum

Ash			2.5%	Maximum		Resistivity:  Less than 50 ohm-cm @ 0 pressure

Sulphur		6.0%	Maximum		Sizing:  100% less than 20 mm particle diameter, 90% less than 2.5 mm, 50% less than 1.25 mm, 20% less than 630 micron

Carbon 		90% Minimum

10.2.2.6	Vent Piping

The vent pipe shall be 25 mm diameter continuous polyethylene.  The vent pipe shall be perforated with four 1/16" holes at 90o to each other and spaced at 2" intervals over the length of the ground bed. The bottom of the vent pipe shall be capped.  The cap connection shall be able to withstand 120 psig.

10.2.2.7	Deep Well Casing

A 200 mm diameter plastic casing shall be installed from surface to a depth of 58 metres.  Each casing joint shall be fastened with glue short, blunt end, screws or by threading the sections together.  The joints have to be sufficiently strong to be able to support the casing string being lowered.

10.2.2.8	Deep Well Surface Casing

A surface casing shall be provided complete with a vented steel top and anode lead wire tie-off bar.  The bar shall be a minimum diameter of 50 mm and coated with extruded PE or wrapped with several layers of PE tape.

10.2.2.9	Positive Anode Splitter Panel

-	The positive lead from each anode and from the rectifier shall be connected in an anode Splitter panel placed near the deep well.  Each anode lead will terminate in its own cable lug and be connected to a common buss bar through a 0.01 or

0.001 ohm/10 ampere shunt.  The rectifier positive shall also be connected to the common buss bar through a 50 ampere/50 millivolt shunt.

-	The panel box shall be painted to the same specifications as the rectifier case and be fitted with single or multiple 50 mm diameter rigid conduit for all cables.  The enclosure shall be dust proof.

10.2.2.10	Negative Splitter Panel

Where there is more than one structure connection at a rectifier site a single negative lead shall be installed between the rectifier and a negative Splitter panel.  Each negative lead, including the rectifier lead, shall be connected to a common buss bar through 50 ampere/50 millivolt shunts.  As with the anode splitter panel, the enclosure shall be dust proof and painted to the same specifications as the rectifier case.  Also, 50 mm diameter rigid conduits will be used as supports and to provide cable entry and exit points from the panel.

10.2.2.11	Surge Arrestors

-	At every electrical isolation joint gas filled spark arrestors must be supplied.

-	The arrestors have to be constructed and connected to the isolation joint or pipe in an intrinsically safe manner to be able to operate under normal circumstances in a Class I, Division I hazardous area.

-	The arrestors must be sized begin conducting at a surge potential of 200 to 300 volts.

-	The arrestor must be able to withstand multiple surges of up to 50,000 amperes.  They are to have a self healing capability.

-	At voltages below 10 volts the arrestor must completely block the flow of electric current.

10.2.2.12	Dual Zinc Rod Grounding Cell

-	To be installed at every electrical isolation joint on the pipe systems.

-	The cells are to be composed of two 35 mm x 35 mm x 1524 mm 'pure' zinc rods separated a distance of 25 mm using dielectric spacers.

-	The rods are to be packaged in a cardboard tube or cloth bag having a backfill of gypsum, bentonite and sodium sulphate.

-	A #8 AWG (8.37 mm2) TWU or TWH cable is to be connected to each rod.

-	The cables are to be connected to the pipe on either side of the isolation joint using bolt or termite weld cable connections.

10.2.3	Material List

ITEM				DESCRIPTION				QUANTITY

1- i)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 65.1 metre leads

ii)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 67.8 metre leads

iii)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 70.6 metre leads

iv)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 73.3 metre leads

v)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 76.1 metre leads

vi)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 78.8 metre leads

vii)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 81.6 metre leads

viii)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 84.3 metre leads

ix)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 87.0 metre leads

x)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 89.8 metre leads

xi)				56 mm x 2133 mm tubular FeSiCr anodes

C/W 92.5 metre leads

xii)				Four (4) Monolythical insulating joints, installed at the beginning of pipeline, upstream and down stream of Pig Receiver/ Launcher at -S-6015 and the forth one at the end of pipeline.

______________

2				30 volt - 12 ampere, oil cooled rectifiers

3				24 volt - 22 ampere, oil cooled rectifiers

4				40 volt - 22 ampere, oil cooled rectifier

5				Rectifier pads - concrete

6				#6 AWG (13.3 mm2) HMWPE Black Cable

7				#6 AWG (13.3 mm2) HMWPE White Cable

8				#8 AWG PVFD & HMWPE Cable

9				3 Conductor #8 AWG (8.37 mm2)

Armoured Cable

10				Single Conductor #8 AWG

(8.37 mm2) Armoured Cable

11				Cable marker tape - English and Arabic

12				Deep well casing - 200 mm x 58m PVC or PE

13				25 mm diameter continuous PE vent pipe

14				Ground bed surface casing 300 mm x

2000 mm

15				Anode shunt boxes c/w 6 circuits

16				Anode shunt boxes c/w 11 circuits

17				Calcimined coke breeze backfill			__kg*

*May increase to 8000 kg if cable drill

rig used

18				#10 (5.26 mm2) AWG TWH White Cable

19				#10 (5.26 mm2) AWG TWH Black Cable

20				Negative splitter panel c/w 7 circuits

21				Negative splitter panel c/w 10 circuits

22				Negative splitter panel c/w 12 circuits

23				Negative splitter panel c/w 3 circuits

24				Dual zinc grounding cells

25				Ground bed pads - concrete

26				Cable marker posts

27				Standard test stations

28				Four wire standard test stations

29				Current monitoring test stations

30				Eight wire current monitoring test stations

31				Two way current monitoring test stations

32				Canal crossing test stations

33				Pipeline crossing test stations

34				Pipeline bonding test stations

35				Termite weld cable connections

36				Mechanical cable connections

37				Transformer oil

38				Single zinc grounding cells

10.3	MATERIAL ACCEPTANCE PROCEDURE

The materials shall be inspected prior to installation by the contractor and Company representative (inspector).

All materials shall be examined to ensure compliance with the specifications, drawings and pre-installation inspection procedure.

After inspection and acceptance of the materials the material inspection check list shall be submitted to the Company for their records.  The list shall be signed and dated by both the inspector and contractor as accurate.

Material and equipment supplied by the Company will normally be consigned to the Contractor at the warehouse or store located on site.  Such material may be consigned contained in their packing, in which case, responsibility for removing the packing shall be the Contractors.

10.3.1	Anodes

-	The size, number and type of anodes to be installed shall be checked for compliance with the specification, drawings and vendor data sheet(s).

-	All anodes shall be inspected to ensure the anode casting shall be metallurgical uniform.  The size of the anodes shall be measured to ensure conformity with that specified.

-	The anode lead cable shall be inspected to be sure that they are free of any cuts or abrasions and that the cable length, size and insulation thickness matches that specified.  Each lead wire should be identified prior to installation.

-	The anode to lead connections strength shall exceed the minimum breaking strength of the connecting cable.

-	The resistance of the anode-to-cable connection shall be checked using an AC resistance meter or Megger.  The resistance of the connection shall not exceed 0.04 ohms excluding the resistance of the cable.  For resistance of copper cable consult standard tables.

10.3.2	DC Positive Cable

-	The size (cross-sectional area), length, type and number of strands of wire and thickness of insulation shall be checked for compliance with the specification, drawings and vendor data sheets.

-	Positive cables shall be checked to ensure it is free of defect, cuts or abrasions.

10.3.3	DC Negative Cable

-	The size (cross-sectional area), length, type and number of strands of wire and thickness of insulation shall be checked for compliance with the specification, drawings and vendor data sheets.

-	Negative cables shall be checked to ensure they are free of defect, cuts or abrasions.

10.3.4	Test Lead Cables

-	The size (cross-sectional area), length, type and number of strands of wire and thickness of insulation shall be checked for compliance with the specification, drawings and vendor data sheets.

-	Test lead cables shall be checked to ensure they are free of defect, cuts or abrasions.

10.3.5	Coke Breeze Backfill

-	The coke breeze shall be calcined petroleum or metallurgical type with chemical and physical properties complying with the specification and vendor data sheet(s).

-	The coke breeze shall be visually inspected to ensure the maximum particle size does not exceed 10 mm and the coke is of uniform colour and texture.

-	The resistivity of the coke breeze shall be measured using a soil resistivity box and AC resistance meter.  The resistivity of uncompressed coke breeze shall not exceed 50 ohm-cm and 5.0 ohm-cm at 5 psig pressure.  See Figure 1, in this Appendix, for equipment connection.

10.3.6	Transformer/Rectifier

-	The rectifier shall be checked for compliance with the specifications and vendor data sheets.

-	The rectifier shall be visually inspected for quality of manufacturing, loose parts or poor electrical connections.  Record all serial and model numbers including as well AC input and DC output information.

-	All mechanical connections should be checked and tightened, as vibrations in shipment may have loosened them.

10.3.7	Anode Current Panel

-	The anode current panel shall be checked for compliance with the specifications, drawings and vendor data sheets.

-	Ensure the number and size of lugs correspond to the number of anode leads and header cables entering the enclosure.

10.3.8	Dual Zinc Grounding Rod(s)

-	The zinc grounding rods shall be checked for compliance with the specifications, drawings and vendor data sheets.

-	The packaging of the grounding rods shall be checked to ensure it is intact and that the backfill is not leaking out.

10.3.9	Vent Pipe

-	The vent pipe shall be checked for compliance with the specifications and drawings.

-	The perforated section of pipe shall be checked for size, and density of the perforation and the length of pipe the perforations cover (should be equivalent to the length of the anode string).  The wall thickness of the vent pipe should be checked to ensure the pipe is of suitable strength and will not collapse during backfilling of the hole.

Deep well Surface Casing

Deep well Sub-Surface Casing

Vented Steel Deep well Cover

-	These items shall be checked for conformity to the specification, drawings and vendor data sheets.

10.4	CATHODIC PROTECTION MATERIALS INSTALLATION PROCEDURES

10.4.1	Termite Weld Procedures

-	Tie test lead wire off to the pipe.

-	Remove pipe coating from top of pipe.  Cut patch at least 2" wide by 3" long.

-	Remove mastic from pipe by cleaning with solvent or by scraping.  File surface of pipe to bright metallic condition.

-	Strip end of wire for approximately 2".  Crimp copper sleeve over exposed wire.

-	Place metallic disk in bottom of welder.  Pour connects of one 15 gm "Cad weld" cartridge into welder.  Squeeze bottom of plastic cartridge to ensure that all remaining contents are placed in the welder.

-	Place welder on cleaned area of pipe and orient so wire slot runs longitudinally with the pipe.  On smaller diameter pipes putty the bottom sides of the welder to stop the molten braze material from running off pipe.

-	Insert wire into cable slot of welder until wire dead ends.

-	With welder lid closed and facing away from operator insert flint gun through opening in lid and pull trigger.  WARNING - WELDER PRODUCES HOT GASES AND METALLIC SPATTER, DO NOT OPERATE WITH FACE CLOSE TO LID OR WITH LID OPEN.  A propane torch can also be used to start the welder.

-	After weldment has solidified on pipe remove welder.  Knock slag off of weld and test weld integrity by tapping with hammer.  If the weld fails do not re-weld at the spot, move a minimum of 150 mm away from previous weld location.

-	File rough edges off of weld.  Coat with mastic or primer and wrap with required outer coating.

-	Installation of two thermo-welds on a pipe, at the same location, should be placed a minimum of 150 mm away from each other.

10.4.2	Test Station Installation Procedures

-	Every two kilometres along gathering lines and the sales line a test station has to be installed unless a current measurement, pipeline crossing, rail road crossing, or parallel pipeline bonding test station exists within 200 metres of the proposed test station site.  Approval for this replacement has to be gained from the Syrian Gas Company.

-	Termite weld the two white leads to the Syrian Gas Company pipeline ensuring to tie each lead off to the pipe so any strain on the lead wire will not affect the weldment.

-	If not previously connected, install each lead to a separate lug on the terminal board.

10.4.3	Current Monitoring Test Station Installation Procedures

-	At intervals of ten kilometres along gathering and sales lines a current monitoring test station is required.

-	These test stations are equipped with two short white leads and two 210 metre long black leads.  The white leads are to be termite welded to the Syrian Gas Company pipeline immediately below the test station while the black leads are to be installed 200 metres down stream from the test station position.

-	The black leads are to be taped to the pipe at regular intervals so they will not be damaged during the construction phase of the project.

-	As with all test stations the cables are to be installed to separate lugs on the terminal boards.

10.4.4	Pipeline Crossing Test Station Installation Procedures

-	At each pipeline crossing location along the sales and gathering lines, whether crossing line is foreign or not, a pipeline crossing test station must be installed.

-	In addition to the procedures for installing a test station, described on page #3, coloured leads have been provided to connect to the foreign pipeline(s).

-	Approval for the method of joining test leads to the foreign pipe(s) will be part of each pipeline crossing agreement.  The coloured leads shall be installed to the foreign pipe(s) in accordance with the foreign companies' wishes.

-	The test leads are to be installed to separate terminal locations along with 5 ohm slide resistors.  The hook up and adjustment of the 5 ohm resistors is the responsibility of the corrosion company which commissions, surveys and adjusts the cathodic protection systems.

10.4.5	Road and Canal Crossing Test Station Installation Procedures

-	At each rail road crossing an appropriate crossing test station must  be installed.

-	This type of test station uses the same installation procedures as for the pipeline crossing test station.  The exception is that the two black leads are to be termite welded to the pipe casing.  This will allow monitoring of the casing.

-	These test stations should be placed at the fence line, if one exists, of the railway right-of-way.

-	As with all other test stations an appropriate concrete bunker shall be constructed around these stations.

10.4.6	Parallel Pipeline Bonding Station Installation Procedures

-	Where a pipeline or pipelines parallel the Syrian Gas Company pipeline, whether foreign or not, a bonding test station must be installed every ten kilometres.

-	These test stations are to be supplied with 5 ohm slide resistors and a set of dual test leads for each line.  The white leads are to be attached to the Syrian Gas Company pipeline with termite welds while the coloured leads are to be attached to the foreign lines using methods approved by the companies owning these lines.

-	Each test lead is to be installed to the test station terminal board in the manner depicted by the appropriate typical drawing.

-	As with the pipeline crossing test stations, the 5 ohm slide resistors will be connected and adjusted by the corrosion company which commissions the cathodic protection systems.

10.4.7	Dual Zinc Rod Grounding Cell Installation Procedures

-	At each location where there is an electrical isolation point on an Syrian Gas Company pipeline a dual zinc rod grounding cell must be installed.

-	The grounding cell comes pre-packaged in a cardboard tube, filled with low resistivity material around the rods, and with two leads extending from the top of the tube.

-	One grounding cell lead is to be bonded to the pipeline side and the other cell lead is to be bonded to the plant side.

-	The grounding cell is to be situated immediately below the isolation joint at maximum lead length.

10.4.8	Single Zinc Rod Grounding Cell Installation Procedures

-	A 13.6 kg zinc grounding cell is to be directly termite welded to the pipeline at each designated crossing location or along the pipeline section parallel to a power line (≥11Kv ) .

-	The cell is to be buried at or below pipe depth as depicted in the typical drawing.

10.4.9	Band Clamp Test Lead Installation Procedures

-	Remove pipe coating in a circumferential strip, 38 mm wide.

-	Remove coating bonding material from pipe by cleaning with solvent or by scraping.  File surface of pipe to bright metallic condition.

-	Strip end of wire for approximately 75 mm.

-	Tie wire off to pipe and loop stripped copper wire several times around stainless steel band clamp.

-	Install clamp around pipe at circumferential strip and tighten.

-	Coat entire exposed area with tar or mastic and cover with repair sleeve or polyethylene tape.

10.5	CATHODIC PROTECTION SYSTEM INSTALLATION

## General

The specifications outlined in this document apply to the installation of all materials required in the deep well ground beds for the Cathodic protection systems.  These specifications are superseded only by the Al Furat Petroleum Company specification outlined in Schedule 'FF' Section 5.  In the event of a conflict between this specification and other specifications the contractor shall consult the owner for a ruling in writing before any work is started.  Where City, County, District or Country codes conflict with this specification the more rigid requirement shall govern.  Any deviation from this specification must be approved, in writing, by owner.

Material quantities are shown on CONTRACTOR’s drawing #_________, Cable Schedule and Bill of Materials, drawings #______, #_______, #_______, #______, #______, #______, #_______ and #_______ and in the Material List in Section 7.2.3.  The quantities may vary due to site conditions.  Further, all dimensions shown must be verified prior to installation.

Any one section of these specifications may be part of or apply to other sections within these documents without being specifically referenced.

The work shall be completed in strict adherence to the all pertinent documents, drawings and codes.  The work shall include but not be limited to:

-	Installation of all Cathodic protection equipment in accordance to the provided drawings and materials and installation specifications.

-	To supply 'as-built' drawings for each construction site.

-	Energization, testing and adjusting of each Cathodic protection system once installed.

All materials should be installed at the appropriate locations shown on the drawings in accordance to installation specifications provided.  Installation of all equipment shall be carried out in accordance to all applicable regulations and codes as pertains to each location.

All excavation and ground work shall be carried out in accordance with Syrian Gas Company Safety Statute and Regulations.  Excavation of all buried pipelines and facilities shall be in accordance with the owners guidelines.

Prior to installation of the cathodic protection equipment each area must be searched and scooped using standard electronic equipment for location of underground lines to ensure that no damage is realised on structures due to the installation of the cathodic protection equipment.

# Rectifier Installation

The rectifiers shall be installed in a non-hazardous areas.  Final position to be approved by Syrian Gas Company to ensure optimum positioning with respect to other equipment nearby.  Unless otherwise specified, the rectifier shall be mounted on a concrete pad.

All AC and DC cables shall enter or leave the rectifier through approved flex or rigid conduit with protective bushings where conduits end.  DC conduits shall extend at least 50 cm below ground surface.

All AC work shall be carried out by a qualified electrician in a workmanlike manner conforming to the appropriate electrical code requirements and industry standards.

The anode cable shall be connected to the positive terminal of the rectifier.  The structure cable shall be connected to the negative terminal.  Additional negative circuits shall attached to the main negative lead in a splitter panel separate from the rectifier.  Sufficient slack shall be left on the cables for servicing.

### Anode Installation

The contractor shall take all necessary precautions to ensure existing facilities are not damaged during excavation or drilling.  The drilled hole shall be a minimum of 250 mm in diameter and drilled to the appropriate depth for each site.  The drilling will be performed preferably by a rotary type rig (Figure 1, Appendix 2), but a cable unit is acceptable, however, a minimum 25% extra coke breeze must be supplied to compensate for non-uniform hole size.  Only fresh water shall be used for the drilling.  No dry drilling will be allowed.  If a rotary rig is used commercially available drilling mud must be used (Figure 2).

Following completion of the hole, a resistivity log shall be conducted to find the appropriate hole sections to install the anodes (Figure 3).  The log shall be completed by applying a constant DC or AC voltage between an anode and a temporary ground bed placed about 50 metres from the hole.  The temporary ground bed shall have a low enough circuit resistance to allow accurate measurement of DC or AC current and voltage while the anode is at the bottom of the hole.

The resistively log would then be completed by raising the anode at 1.5 metre intervals and recording the voltage and current.  The resistance at each depth is then used with Graph #1 to calculate the soil resistivity in ohm-cm.  A copy of each log shall be presented to Syrian Gas Company.

Once the resistively log has been completed the 200 mm diameter bell and spigot plastic casing shall be installed in the hole.  Each section of the casing shall be lowered in with the bell end up.  this casing is to extend a minimum of 58 metres into each hole.  The 300 mm diameter surface casing is to be installed over the well casing pipe.

After placement of the well casing the hole shall be flushed with fresh water to remove drilling mud and cuttings (Figure 4).  The anodes are then to be placed in a string at a separation of at least 60 cm between the top of the lower anode to the bottom of the upper anode.  The anodes are to be placed in well sections demonstrating relatively constant and low soil resistivity (<10,000 ohm-cm).

The 25 mm, continuous vent pipe shall be lowered with the bottom anode (Figure 7).  Using glass filament re-enforced tape, the vent pipe shall be taped to the deepest anode.  The bottom of the vent pipe shall be sealed and glued with an appropriate sized cap.  After each anode has been lowered, it is to be tied off to a support bar until coke breeze consolidation (Figure 8).

After installation of each anode, calcined coke breeze shall be pumped using a trash pump such as a Gorman-Rup into the hole through a pipe which has been lowered to the bottom of the well (Figures 9 & 10).  The coke breeze shall be mixed with water at a ratio of 27 litres of water to 45 kilograms of coke breeze.  The pipe is to be raised at a rate equal to the rate that the hole is filled with coke breeze.

After sufficient time for the coke breeze to settle, the resistance of each anode lead to ground shall be measured to ensure that all of the anodes are in the coke column.  If necessary, pour additional coke breeze into the hole to cover all of the anodes.

Once the coke column has stabilised, approximately 24 hours, the anode leads shall be released and then supported permanently by bundling the leads together, wrapping electrician's tape around the bundle for a length of 24 inches, and wrapping the taped lead section around a 50 mm diameter, polyethylene coated, steel bar.  The bundled leads would then be brought together, under the bar with the leads coming out of the well.  The lead bundle would then be wrapped over a length of six inches with three layers of glass filament re-enforced tape.  The leads would then exit the well casing and be installed in to a current splitter panel.

Excess dirt from the augured hole shall be either removed from the site or redistributed over the excavated area to the satisfaction of the owner.

## DC Cable Installation

Buried DC cables shall be installed to a minimum depth of 60 cm and shall be laid to follow the contours of the trench leaving reasonable slack for the cable.  Care is to be taken when back filling cable to ensure that rocks do not damage cable insulation.  Cable warning tape shall be buried above each cable.

The positive cable shall be continuous with no spliced joints between the rectifier and the anode splitter panels unless splicing is approved.  All anode lead cables shall remain free of splices, nicks or other physical damage.  All cables shall be visually inspected for nicks, cracks, or abrasions in the coating before installation.  Positive and negative cathodic cables installed above ground level shall be protected from mechanical damage with suitably sized rigid conduit.

RESISTIVITY GRAPH

1

10.6	CATHODIC PROTECTION SYSTEM COMMISSIONING

## SURVEY TECHNIQUES

In order to conduct a comprehensive adjustive check survey on a clients facilities, the following procedure should be utilized:

-	Review design and follow commissioning instructions for the cathodic protection system.

-	Contact the client to arrange a schedule.

-	Prior to beginning survey ensure that all necessary equipment is in working order and available.

-	Complete a detailed rectifier check.  The rectifier check should consist of:

As Found Readings

Actual Output

As Left Readings

Manufacturers' Data

DC Cable size, colour and tie-in point to the rectifier

Rectifier general operation

Efficiency testing

-	Visual Inspection and Maintenance of the unit should include:

Latches, hinges

Condition of the rectifier case

AC and DC connections

Proper rectifier mounting

AC breaker and power meter conditions (if applicable)

Lubrication of mechanical parts (if required)

Overall appearance

Integrity of connections

Proper operation of the AC breaker within the rectifier

Transformer check

Stack assembly conditions check:

- Selenium:  blistering, hot spots, colour variations

- Silicon:  hot spots

Meter condition

Switching condition check

Cleaning of oxide layer/build-up on rheostats and terminal connections

Is the post straight or requires replacement

Other general construction requirements.

-	Prior to rectifier energization for new pipelines where a cathodic system has recently been designed and installed, the static (native state) potentials must be measured at all access points on the gathering system.  After the static survey has been completed, set rectifier to target current recommended in design report.

-	Once the operation of the rectifier is acceptable, begin survey at one end of the pipeline ensuring that all incoming lines are properly isolated, the grounding cells are in place and structure-to-soil potentials are acceptable.

-	Interrupt the DC current output of the rectifier.  If multiple rectifiers exist, synchronize current interruption.

-	Take current 'ON' and 'OFF' structure-to-soil potential readings all the entire pipeline and spur lines.

-	Potentials (ON/OFF) should be recorded at the following locations:

-	Headers

-	Risers

-	Test Points

-	Road & Railway Crossings

-	Foreign Pipeline Crossings

-	Foreign test points near Syrian Gas Company line

-	Interference control bonds

NOTE:	Show the full legal descriptions at each location as this helps the clerical staff significantly.

-	Line continuity:  If there is no ON/OFF shift on a line section it is probably not electrically continuous with the cathodic circuit.  The location of the discontinuity should be determined and a bond should be installed (refer to Electrical Continuity Section for detailed testing procedures).

-	If there is an interference control test station at a pipeline crossing, complete the following:

-	Take as found/ON-OFF foreign and line potentials.

-	Determine the magnitude and direction of current flow through the test station.

-	Disconnect the interference bond and retake the foreign and line potentials.  For evaluation of this data see section on mitigation of electrical interference.

-	If necessary, perform over the line, close interval, potential testing to help determine extent of interference.

-	Foreign Rectifiers:

-		Take on-off structure-to-soil potential readings with and without the foreign rectifier operating.  If stray current interference is noted with the operation of the foreign rectifier note this and correct situation if possible.  If the condition is very critical contact client immediately for further instruction.

-	Check the general condition of all cathodic protection materials and note what is required to upgrade those areas of concern.

This should include:

-	Above ground test stations, above ground bonding which does not meet client requirements.

-	Crooked test station and rectifier posts.

-	Any other construction practices which do not meet client specifications.

-	Check the as-proposed drawings and revise if they are not accurate.

-	If protection has not been established over all of the gathering system increase the current from the rectifier.  As a guide line for coated pipelines, the current requirements will be approximately 30 microamperes per square foot.

-	Once the current has been established, the drain point potential should be checked and should not exceed -2500 millivolt, referenced to a copper-copper sulphate reference electrode, unless extenuating circumstances such as lack of suitable ground/rectifier locations or high current requirements are encountered.  The current should be set to allow a minimum polarised potential of -850 millivolt to be obtained at each test post.

REFERENCE ELECTRODE CONTACT RESISTANCE

The surface soil upon which the reference electrode is placed is often dry, and consequently has a high resistivity compared to the soil at pipe or cable depth.  The effect of this surface condition is to introduce an unknown high resistance into the external measuring circuit.  Meter manufacturers recognise this problem and now manufacture electronic meters which are much more sensitive than older meters.  In most cases, this has solved the problem although there are some locations where errors are still present because of contact resistance of one megaohm or more.  This type of error can be detected by taking measurements with two difference input resistance.  On older, non-electronic meters, the readings taken on two adjacent ranges can be compared.  Regardless of the methods employed, if the two readings do not agree within less than 1% it means that there is a contact resistance error.

A practical method of minimising contact resistance errors is to wet down the area of electrode contact with tap water or to dig a small hole and place the porous plug of the reference electrode in contact with more moist soil beneath the surface.

IR (VOLTAGE) DROP PHENOMENON

Pipe-to-soil potentials measured against a reference electrode placed on the soil when the protective current is switched on always incorporates an IR drop caused by the ground resistance, the coating resistance, the holiday resistance and the resistance in the metallic portions of the circuit.

A single measurement of the pipe-to-soil potential on a coated pipeline made at ground level will yield a value that is the average bare surface potential of coating defects which can be located tens and even hundreds of meters away.  Variations in potential over the pipe surface, caused by holidays of difference size in coated pipe, will give rise to different potentials as measured at ground level over different parts of the pipe.  For the cathodic protection of pipelines it is therefore essential to measure the pipe-to-soil potential accurately.

As a result of the IR drops which will exists, the measured pipe-to-soil potential will be considerably more negative (particularly in the case of high resistivity soils or poorly coated pipelines) than the potential at the metal/electrolyte interface.  The problem is therefore when and how to eliminate the influence of the IR drop component in the measured potential in order to ensure accuracy of the readings.

COMPONENTS OF THE PIPE-TO-SOIL POTENTIAL

The pipe-to-soil potential at a coating holiday consists of the following components:

Eon = Eo + Ep + Es = Eo + RpI + RsI

where

Eo	=	Free Corrosion

Ep	=	Electrochemical polarisation

Es	=	Voltage drop in soil

Rp	=	Polarisation resistance

Rs	=	Soil resistance

I	=	Constant protective current

The sole measure of the effectiveness of cathodic protection is the electrochemical polarisation and the foregoing equation at time equal to zero reduces to:

Eoff	=	Eo + Ep

or the real potential at the metal/soil interface can be measured immediately after the protective current has been switched off if the pipeline has been polarised evenly.  Potentials will still vary in the case of pipelines laid in different soil with coating holidays of different sizes because even polarisation will not exist.

It can be appreciated that the on potential, or the potential with the cathodic protection current applied, can assume values ranging from the free-corrosion potential of -0.4 to -0.6 volt (Cu-CuSO4) to several volts with the most negative values depending only on holiday area and available current.  Although there is really no limit to the magnitude of the potentials with current applied, the true polarised pipe-to-soil potential or the potential measured the instant the cathodic protection current is switched off, appears to be limited to values from the free corrosion potential to about -1.1 to -1.2 volt.  The apparent reason for a limiting potential is that, under cathodic control, the true potential of the steel becomes fixed by the environment developed at the steel surface.

It is possible that, in some cases, potentials more negative than -1.15 volts, after correction for IR drop, will be observed on pipelines although in most instances all current to the pipeline cannot be shut off due to stray currents, multiple protection systems, galvanic ground beds and current flow between the smaller or more polarised coating defects and the larger or less polarised coating defects.

With a limiting potential known to exist it is apparent that potentials recorded with magnitudes in excess of -1.1 to -1.2 volts (Cu-CuSO4) are being affected by either extraneous current sources or contain an IR component.  This IR component increases with coating holiday size and with electrolyte resistance with the consequence that recorded potential values with protective current applied may be too negative.

As previously noted the measured pipe-to-soil potential is made up of three parts; the IR drop component, the polarisation potential and the free corrosion potential which add algebraically to give the measured pipe-to-soil potentials.  The IR component results from the fact that a potential gradient must exist in the soil in order to have current flowing to the pipe but this IR component can be eliminated by making I = O if all current to the pipe is shut off, or by making R = O, if the reference electrode is moved extremely close to the controlling holiday on the pipe.  If the IR component is reduced to zero the measured pipe-to-soil potential would be the true pipe-to-soil potential at the interface between the steel and soil environment.  On coated pipelines installed in high resistivity soils or having numerous or large holidays, the lack of IR drop correction can yield pipe-to-soil potentials which are more negative than actual.

COMPENSATION TECHNIQUES

Numerous techniques have been employed to remove the unwanted IR drops from pipe-to-soil potentials but many of the techniques are time consuming, expensive and cannot be undertaken using simple measuring instruments.  Following are some of the conclusions of various investigators:

-	Pipe-to-soil potentials measured against a reference electrode placed on the soil always incorporates an IR drop caused by the ground resistance, the coating resistance and the holiday resistance, if applicable, and resistance in the metallic portions of the circuit.

-	The IR drop component can be eliminated by making I = O, if all current to the pipe can be shut off, or by making R = O, if the reference electrode is moved extremely close to either a bare pipe or to the controlling holiday on a coated pipe.

-	The true polarised potential on a pipeline is limited to values that range from the free corrosion potential to -1.1 to -1.2 volts (Cu-CuSO4) indicating that higher measured potentials contain an IR drop component or are being affected by extraneous current sources.

-	Interrupting the cathodic protection current source yields IR drop free pipe-to-soil potential values on bare or poorly coated pipelines only if no extraneous current sources exist.

STRAY CURRENT INTERFERENCE

Interference currents and stray currents may be defined as man-made electric currents performing work on one grounded plant, which flow on other nearby grounded structures using electrolytic earth paths for interconnection.  The currents may be separated into static currents, which maintain constant amplitude and geographical paths such as cathodic protection rectifier-ground beds, and dynamic currents which have variable amplitude and/or continually changing geographical paths such as DC generating equipment or electric railways.  Whenever a pipeline lies within the path of such currents, there is an opportunity for current to enter and leave the line; at the points where it leaves, it will corrode the pipe.

Because of the inherently accidental or unintentional nature of dynamic currents, they are usually known as stray currents, and the damage they do is known as stray current electrolysis.  Direct currents introduced deliberately into the earth for the purpose of applying cathodic protection to one structure are also capable of doing great damage to other structures which occupy the same earth.  This is not strictly 'stray current'; the damaging effect is accidental but the presence of the current in the earth is not accidental and these currents are commonly known as interference currents.

DETECTION OF STRAY CURRENTS

Whenever the measurement of any of the electrical quantities connected with a pipe line, such as line current or pipe-to-soil potential, shows fluctuating values, there is a case of stray current at hand.  Often it is very helpful to leave the meter connected to the structure or install a recorder in order to monitor the fluctuations.  The rapidity and nature of the changes will frequently give a clue to the origin, and it may be that the actual operation of the offending system can be observed; for example, the change when a street car passes or the cessation of fluctuation for the noon hour may locate the source.  By the application of similar reasoning to records of several successive days, it is usually possible to track down the DC system from which the stray current is coming.

DETECTION OF INTERFERENCE

Interference may be suspected if higher than normal negative voltages are observed on structures or conversely if lower than normal negative voltages or any positive voltages are evident.  It should be remembered that a situation which results in a more negative structure potential indicates that current is flowing from the electrolyte to the structure under test and a less negative structure potential indicates that current is flowing from the structure under test to the electrolyte.  Under this latter circumstance corrosion of the structure may occur.

Whenever there is current flow in the earth, a piece of metal buried in that earth may function as a part of the current path collecting current over a part of its surface and discharging it, with attendant corrosion, from another part.  The amount of current picked up and discharged is controlled by many factors; the coating, if any, on the structure; the length of the structure in the direction of current flow; the potential gradient or the current density at the point of exposure; and the ability of the structure to carry current.  A bare pipeline, lying in the direction of current flow, close to an anode bed (where the current density and potential gradient are great) is in a very hazardous exposure; a well-coated line, remote from an anode bed, and traversing the current field at an angle, is much less seriously endangered.

The problem of interference is simpler in many respects than that of stray current.  The exposure is, in general, steady rather than fluctuating, so that more accurate measurements and adjustments can be made.  The source of the current involved is under control; the rectifier can be switched on and off as desired, or an interrupter may be used so that the effects of the unit can be clearly identified and studied.  Under the worst conditions, the exposure can be extremely severe, because of the magnitude of the currents involved; all of the current return is by the earth path, instead of merely that portion which leaks off, as with stray currents.

Many companies arbitrarily select a potential shift value whereupon the interference current must be controlled if this value is exceeded.  Considering that potential levels comprising an interference shift are based on factors such as cell placement, soil resistivity and electrolyte current flow, selection of an arbitrary number is not a valid method of interference evaluation.  Each specific interference situation must be evaluated in detail and assessed as to adverse effects and control.  For example, a structure possessing a high negative potential can withstand a much greater positive potential change than can a structure which has a negative potential at or near the minimum criterion for protection without suffering adverse affects.  Some companies consider that the positive shift represents specific current discharge from the affected pipe rather than merely a reduction in the net current flow to the pipe.

By definition, a buried or submerged steel structure is assumed to be Cathodically protected when the polarised potential at all points on the surface is a least as negative as -0.85 volts measured with respect to a copper-copper sulphate reference electrode.  If the potential is not driven more positive than -0.85 volts to a copper-copper sulphate reference electrode, corrosion cannot occur.  In marginal situations, there must be a concern for the accuracy of the potential measurement as the true potential at the pipe surface will be less negative than the potential measured with the reference cell placed at grade directly over the discharge point.

DETERMINATION OF POINT OF MAXIMUM EXPOSURE

When a potential increase is noted on a structure, with the interference current source operating, concern must exist as to the location of any point of current discharge as corrosion occurs where current leaves the structure and flows into the surrounding electrolyte.  The geographic site of the most adverse electrolytic effect corresponds to the place where the bulk of the interference current is leaving the metallic structure.  This point can be determined by interrupting the interference current source and observing structure-to-electrolyte potentials over the suspected drainage area.  The site where the maximum potential change in the less negative (positive) direction occurs when the source current is applied is the geographical location of the maximum exposure.  Regardless of where mitigation of the problem is undertaken, the structure-to-electrolyte potential clearance must be observed at this location.

CRITERIA

Three criteria are commonly used in determining the adequacy of mitigate action.  First, the 'NO SWING' criterion may be applied.  This requires that the potential of the affected pipeline does not shift in the positive direction when the foreign rectifier cycles from off to on.  This criterion is reasonably applicable to well coated pipelines but may be unnecessarily severe.  Second, a 'NATURAL POTENTIAL' criterion may be applied.  The affected pipe is to be returned to the potential existing before the interference began.  In many cases the natural potential may be very difficult to determine.  Third, a 'NO CORROSION' criterion may be applied.  If a mitigate measure can be demonstrated to produce conditions under which corrosion is electrochemically impossible, it should be accepted as adequate.  This criterion is only applicable to protected structures and other consideration must be applied to unprotected structures subject to interference.

MITIGATION OF INTERFERENCE

When it has been established that interference exists and the location of the area of most adverse effect on the interfered structure has been determined, a way must be provided for the interference current to flow from the metal of the affected structure by non-electrolytic conduction.

Electrolytic corrosion occurs where current flows from metal to electrolyte, therefore, a more attractive pathway must be offered to the interference current at its metal-to-electrolyte exit.  A metallic conductor will offer this more attractive exit if it is terminated where polarity is correct and strong enough to draw sufficient current through the conductor.  When a foreign cathodic protection rectifier is the source of interference, the protected structure is an extension of the negative terminal of the source.  Drain (or bond) conductors are usually installed at the crossing of interfered and interfering structures so that length of bond leads must be kept short, offering the least possible resistance to current flow.

Sometimes a 'solid' bond is used; i.e. one without a resistor.  This usually results in affording a considerable measure of cathodic protection to the foreign structure and, if it is bare or has poorer coating than the protected structure, it may received too large a share of the current.  Ideally just enough current should be drained across the bond to prevent inflicting any damage in the foreign structure; to do so requires the use of a resistor in the bond.

The bonding method, which is used extensively, is always of some benefit to the interfered structure and always of some detriment to the protection system of the interfering structure.  Many factors determine the degree of benefit and detriment such as proximity of ground bed to foreign structure, rectifier current output, and coating resistance of both structures.

To adjust a resistance bond requires that a copper-copper sulphate electrode be placed in the electrolyte at the point of crossing.  For pipelines this will usually involve an excavation, exposing a vertical wall of soil where the two lines are closest, although sometimes a long electrode can be properly placed in a rodded hole.  The connections to the two lines are made, and the resistor is adjusted until there is no change in the potential of the foreign line, with respect to the electrode, when the rectifier is switched on and off.  The pipe connections are usually made by the termite process, and Chromel or Nichrome wire is used for the resistor.  It is much easier to determine the length of resistor wire needed by trial and error than it is by calculation.

Mitigation is also possible by other methods than the bonding method.  If all structures were flooded adequately with their own protection current, and all foreign current draining areas were maintained more negative than -0.85 volt, there would be no detrimental interference and no mitigation measures would be necessary.

It is becoming common practice to install galvanic anode drains in lieu of bonds where small drain currents flow.  Large drain currents would corrode the galvanic material rapidly requiring impractical frequent replacement.  The 'natural potential' criterion for indication of interference clearance may be used with galvanic drains or rectifier drains as well as with resistance bonds.  The use of galvanic anode drains eliminates interconnection of owned and foreign structures with the inherent benefits and/or detriments.

10.7-CATHODIC PROTECTION DRAWINGS

All Drawings in this section, shall be supplied by the CONTRACTOR