11-	INSTRUMENT AND CONTROL SCOPE

11.1	GENERAL DESCRIPTION

11.2	JOB DESCRIPTION

11.3	TESTING, COMMISSIONING AND START-UP

11.4	FIELD INSPECTION

11.5	DRAWINGS

11.6	CONTROL EQUIPMENT SPECIFICATIONS LIST

11-CONTROL SYSTEM

11.1	GENERAL DESCRIPTION

    - -Scope

This section of the contract will define the minimum requirements of control system for the ARAB GAS PIPELINE PHASE II project. It will include the Controls, Metering, and Gas Compression Systems with interfacing to the existing SCADA and Telecommunication System of GAS CO-ORDINATION CENTER near HOMS city, New Fiber Optic Cable will be laid alongside the pipeline for Telecommunication, Control and data transferring.

The project shall mainly consist of, but not be limited to:

-Fiscal Metering Station at ALforeqls (FMS).

-Gas Compressor Units at ALforeqls.

-Two Pig Launchers.

- Two Pig Receivers.

-Four Block Valve Stations.

-Fibre optic cable and Telecommunication System.

-PLC/DCS Control/Monitoring and Emergency Shutdown Systems.

-Mechanical connection with Existing Future connections at ALforeqls.

11.1.2-Codes, Standards and Documents

The control system, including equipment, design and installation shall conform to all applicable RFQ specification, United States and International Codes and Standards including but not limited to that specified and described in the “EXHIBIT-G, Data References and Contract’s General Specifications” and in the “Exhibit-F, Appendices and Special Project Specifications”.

In case a discrepancy arises or exists between codes, standards, drawings and documents, the most severe shall govern.

11.1.3-Materials and Products

CONTRACTOR shall provide all materials, personnel, tools and construction equipment for the installation of the controls, metering systems in accordance with Drawings, General Specifications, Codes and Standards.

CONTRACTOR shall identify critical items of equipment and other materials and shall make appropriate arrangements to order and have such items delivered to meet the required overall completion date.

11.1.4-Construction

CONTRACTOR shall provide all personnel, supervision, co-ordination, tools and materials as well as competent knowledge of construction for the installation, testing and putting into operation of each control and telecommunication systems and products specified.

CONTRACTOR shall execute all work in a workmanlike manner so as to present a neat and finished appearance when completed.

CONTRACTOR shall become familiar with the Construction Drawings of all trades and when laying out the work with regard to structural, piping and mechanical features.

CONTRACTOR shall provide for approval a construction schedule, which will take into full consideration the availability or delivery of all equipment, materials and the target completion date required by the COMPANY.

CONTRACTOR shall arrange his own inspection team and equipment for the quality control of the whole work. It shall be noted that, although the COMPANY will appoint its own independent inspection agent, the responsibility for meeting the appropriate quality standards will remain with the CONTRACTOR.

CONTRACTOR shall perform the commissioning and start-up activities to the satisfaction of the COMPANY or its representatives.

11.1.5-Environment

All Equipment (devices, instruments) and materials shall be designed to fulfil the environmental specifications and conditions provided in “EXHIBIT-F and EXHIBIT-G”.

11.1.6-	Typical Gas Composition

The FMS's, Compressor station will be supplied with gas as described in EXHIBIT-  G  It is the Contractor’s responsibility to ensure that the whole project is designed  to handle these type of gases. Sizing and calculation shall be based on the worst case.

11.1.7-   Material Selection

All material and equipment/instruments supplied for the ARAB GAS PIPELINE PHASE II project shall be suitable for the conditions (environmental, site and gas) as defined in the “EXHIBIT-F and EXHIBIT-G”.

11.1.8-Project Schedule

CONTRACTOR shall provide a complete schedule as indicated in section 1-General Scope and Definition.

11.1.9-Drawings

CONTRACTOR shall provide the Drawings as required “AFPC Schedule-B, Engineering Documentation” provided in “Exhibit-G, Data References and Contract’s General Specifications”.

Contractor shall provide "As-Built" drawings, to cover the information for the following items and as minimum:

-Device, instruments and equipment locations and layout.

-All configuration/programming changes

-All control panel layout changes

-All loop drawings changes

-All underground cables layout

-All cables routing changes

11.2    JOB DESCRIPTION

11.2.1	General

This section deals with the following Company’s required items as minimum:

-Instruments for pipe line, launchers, receivers, intermediate station, and BVS's.

-One FMS ALforeqls.

-Three Gas Compressor Units at Al FOREQLS with all Instrument and control (PLC) systems including anti-surge system.

-Ultrasonic Gas Flow Measurement for the FMS's.

-On line chromatograph for  FMS.

-The integrated microprocessor based control system (Distributed Control

System (DCS)).

-Control panel(s) and Shutdown system for  FMS.

-Gas detection and fire fighting system for  FMS.

-interfacing (Full Integration) with the SCADA system of GAS CO-ORDINATION CENTER.

11.2.2	Detailed Scope of Work

The following is the division of responsibilities between CONTRACTOR and COMPANY.

- COMPANY

-Provide Design Guidelines.

-Review and approve basic and detail design.

-Review and approve specification and requisitions.

-Review and approve Vendor selection.

-Monitor progress as per schedule.

2- CONTRACTOR

-Obtain Approval from Company for Requisition Package.

-Submit work schedule.

-Procure System.

-Program/Configure Systems

-Develop Factory Acceptance Test (FAT) and Site Acceptance Test

(SAT) procedures for DCS system and obtain COMPANY approval

-Submit FAT/SAT documentation to COMPANY for approval

-Perform FAT at Vendor's facility and SAT at job site

-Install and commission equipment

-Provide all engineering documentation to COMPANY

-Generate As-Built drawings/documents and submit to COMPANY

-Submit SPIR forms for Company’s approval

-Training for operating and control Systems at Vendor’s Workshops fully accommodated, except flight tickets, which shall be provided by Company

-Contractor shall design, procure, deliver, install and commission the followings as outlined hereafter:

A-	AL FOREQLS FISCAL Metering Station (fMS)

# General Description

The FMS Station shall be manned. A gas compressor Units will consist of three compressors-3X50% (Two compressors in operation and the Third as stand-by capacity of 4 BCM / Y ) with  all related facilities.

The compressor Units facilities should be designed and constructed to allow for future expansion by installation and connection another additional Two Gas Compressor units (to increase the capacity up to 8 BCM/Y) without any modifications to the suction, discharge, electrical, fuel gas systems, control and monitoring, DCS and telecommunication . . . etc. systems and facilities as further described in this RFQ in order to increase the Pipeline capacity to be able for transportation of 8 BCM / Y.

Generally, in sizing, installation, and construction of all equipment and systems Contractor shall take into consideration the provision and spare space for future installation of Two Gas Compressor units.

The Control system will be microprocessor based electronic distributed control   system (DCS) and pneumatically actuated shutdown valves. The shutdown valves will have electrical solenoids for activation.

The WORK to be included in the CONTRACT embraces, but is not limited to engineering, design, procurement, transport and delivery, construction, installation, testing and inspection, pre-commissioning, commissioning, Start-up, documentation, warranty and hand over.

The emergency shutdown system shall be stand-alone inherently fail-safe system, with dedicated transmitters interfaced to the DCS system through Modbus for monitoring and SCADA transmission.

Contractor shall supply and install fire and gas detection system and fire gas suppression system.

Flow metering will be by using Ultrasonic Flow measurement as per AGA-9 for each meter run and each run of fuel/instrument gas skid.

All items associated with the packages/metering station shall be mounted on skid(s), be fully accessible for maintenance from integral platforms and completely tested.

Contractor should note that, to ensure maximum reliability of control systems, all instrumentation shall be installed off-skid in an area easily accessible for operator intervention.  All electronic instrumentation and local control panels shall be equipped with sunshade.

The control facilities shall include a standalone ESD System, to protect the facilities when emergency situations occur.

The contractor shall provide a pressure and temperature transmitters at each downstream of BVS's including the launchers and receivers, intermediate station, those signals will be transmitted to the control room of FMS's and Existing GCC- SCADA system.

Contractor shall provide a station blow down system in case of ESD, which shall be connected to the flare stack situated to the safe area.

A common vent system capable of relief sufficient gas to prevent over pressure in the event of 5 % leakage over the pressure control valve and failure of the train SDV shall also be included. This common vent system shall be connected to each meter trains, compressors with the flare stack. The flare stack area shall be graded and fenced in accordance with specifications.

All inlet of major equipment shall be equipped with double block and bleed valves for easy maintenance, as minimum for the following main equipment:

-Inlet and outlet of gas compressor units.

-Each train of metering skid.

- Each train of Fuel/Instrument gas skid.

Site training shall take place before station commissioning in order that COMPANY operating staff gain “HANDS ON” experience.

### A-1     Metering Trains

###### System Description:

The facilities will consist of three main metering trains-(3X50%), two in operation and the other standby

Each train shall include an independent meter run. Each run shall contain one filter separator (Cartridge type) with automatic drain valve for liquid, Ultrasonic flow meter(s), One (1) On line gas chromatograph Package, one emergency shutdown valve (ESV) at the inlet of train and one emergency shutdown valve (ESV) at the outlet of train, vent and blow down system and all related piping, instrumentation, valves,… etc.

The gas chromatograph should be as a package in one Cabinet (one in operation and the Second as stand-by), all data or results of gas analyzing shall be transmitted to the Flow computer and to DCS and GCC as well.

The filter separator shall remove solids to ensure that the outgoing gas stream shall contain less than 30 PPM by weight and a particle diameter less than or equal to 10 microns.

Downstream of the shutdown valve shall include a metering facility and a high-pressure trip (using dedicated smart pressure transmitters) to actuate the train inlet/outlet shutdown valves, in case of pressure build up to a level unacceptable.

The metering trains will take gas from the different sources and delivered to the gas compressors.

Each metering train shall be capable of total design capacity up to 230000 SCM/H.

Each individual duty train will have its production rate set by demand.  The Control System is expected to respond instantly to demand variations, including Compressors ESD.

Variations around the set delivery Flow Range should not exceed such value to ensure reliable and smooth gas feeding process.

Process and Control Requirement:

The objective of the Control System is to secure the continued supply of gas demand at levels depicted by the Compressor units, in a manner which does not require the intervention of operational staff during steady state and/or transient conditions. Hence, the Process Control System shall   accomplish the required tasks in a fully automatic mode.

CONTRACTOR shall provide calculations to demonstrate that the system can react fast enough to prevent over-pressurising of the down-stream facilities and to make any modifications to the design to meet this requirement.  It shall be the responsibility of the CONTRACTOR to gather the relevant information to allow these calculations to be made.

Strategy:

On initial start up, the gas will be delivered via The one metering  train, shutdown valves shall be opened, the flow rate will be  able to start from zero to full load (50% of FMS Capacity), when the control system receive the open signals from the first train shutdown valves , the DCS will give a permissive signal to start one of the compressor units (50% of FMS  capacity), when the DCS receive the run status of the first compressor, then DCS will open the valves of second meter train to provide the necessary gas for compressors operation (100%), when the second meter train valves are opened , the DCS will need a confirmation to give the permissive to operate the second compressor, in this Case we have two compressors in run mode, and two meter trains in run mode, when the outlet pressure of the compressors  reach the demand value (the set point of the outlet pressure), then the outlet shutdown valves of the compressors  will open, recycle valves at the inlet of compressors will be open 100% on initial start up, and start to close automatically when starting to load the active  compressors.

The operator can operate one meter train and one compressor only (50% of FMS Capacity) with the same level of continuous safe operation according to the demand of pipeline supervisor, especially When the gas flow rate equal or less than 45 % of the FMS Capacity.

The normal operation conditions with full capacity of the FMS will be:

-Two metering trains in operation mode.

-Two Gas compressors in run mode and the Third in stand-by mode.

-The remaining metering train (third one) in stand-by mode and

Its outlet shutdown valve should be open.

-One fuel/instrument gas train will be in run mode and the Second in

Stand-by mode.

The compressor will be able to operate remotely and fully automatic from the control room of ALFOREQLS FMS; the control system of the compressors will be standalone system and interfacing with DCS /ESD systems of the FMS.

It shall be possible, on operator’s request to manually bring on line the standby equipment (train on the metering skid and fuel/instrument gas skid, stand-by compressor)

Also, in the event of one train shutdown, an automatic change over to the standby train shall be initiated, the Electronic Control System having the necessary interlocks and permissive built in.

The Electronic Control System shall be so designed as to prevent gas supply to the consumers from being affected by load changes, operator’s adjustment train changes over or imposed limits.

The contractor is responsible to make all necessary configurations (mechanical& control) for operability of the FMS without compressor units in case of the gas consumption is very low, and the pressure is suitable for operation without compressor, this possibility can be made as following:

From the initial start-up of the FMS the operator can put the compressor units  in override mode, then the DCS system of the FMS will bypass the compressor operation with all related function, in this case any maintenance or check procedure for the compressors (or one only) should not effect the operation of the FMS, an automatic shutdown valve shall be installed on the bypass line of the compressor units, this valve will be open automatically when the compressor override via DCS system, or the status of all compressors are normal stop or emergency shutdown status.

Control Concept:

The Control system should have two scenarios for FMS operation:

I-with one or two Compressors.

II-without compressors.

The Control System shall be so designed that on initial start up, the sequence of process operation should be but not be limited as following:

I-with one or two compressors:

-For full capacity: -bring on line the first meter run.

-bring on line the first compressor.

-bring on line the second meter run.

-bring on line the second compressor.

-For 50% of capacity: -bring on line the first meter run.

-bring on line the first compressor.

II-Without compressors: -set the compressors to override or Normal stop or Emergency stop.

-open the first meter run.

-open the by-pass automatic shutdown valve.

As soon as the Control System Receive the open signals of one meter runs shutdown valves then the Control System shall bring one of the Gas Compressor units on line, and still allowing for a continuously increasing flow demand.

The Second meter train shall be brought on line when the second compressor is in run mode and flow rate reach more than 45% of the FMS Capacity.

The third meter runs can be brought on line in the same way as per operator request.

The Control System shall be fast enough to respond to an uncontrolled trip of a Compressor or its outlet.

The inlet of FMS shall designed for minimum inlet pressure of 30 Barg up to 45 barg , The FMS station shall be designed for a set delivery pressure comprised those values from pipeline operating pressure .

The main shutdown valves shall be designed and sized to provide feeding gas to the Compressor units from zero (0) up to (460000SCM/H).

Contractor shall design, procure and install the fire and gas detection system and   automatic gas suppression system in the FMS Station (including compressor station).

### A-2      fuel/Instrument Gas System:

Contractor shall provide a fuel/Instrument gas System consisting of two trains, each train typically consists of: one electrical heater, one pressure reducing system (two stage pressure reducing Throw self containing pressure control valves), two shutdown valves at the inlet and outlet, gas flow measurement (ultra sonic preferred, other wise the flow shall be according to ISO 5167), one (1) filter drain, with all related piping, instrumentation, valves, etc.

The filter separator shall remove solids to ensure that the outgoing gas stream shall contain less than 30 PPM by weight and a particle diameter less than or equal to 10 microns.

Each filter drain shall be provided with a manual drain valve, pressure gauge.

Gas operating pressure shall be 4.5 - 7 Barg; Contractor shall provide multistage pressure reducing instrument system. Contractor shall ensure that, from black-start (de-pressurised) conditions instrument gas pressurisation can be accomplished without resorting to the use of bottled gas.

Contractor shall design the fuel/instrument gas skid to provide a fuel gas for the gas compressor units in the capacity of 4 BCM/Y, with future Expansion to increase the FMS Capacity up to 8BCM/Y by adding another two gas compressors.

Contractor shall be provided a buffer tank with capacity 110% of gas consumption required for fuel/instrument supply for period of time to stop the running compressors in safe condition, in case of (PCV's) failure.

- C-  DCS,ELECTRONIC CONTROL AND MONITORING SYSTEM:

Distributed Control System (DCS) shall be used for automatic control and monitoring of all data and parameters of the project and shall be installed in control room of  FMS's  and  interfaced (Full Integration)   to the existing SCADA system of GCC in order to monitor all data and parameters of the project in all GCC workstations.

Contractor shall be responsible to supply and deliver all hardware, software and any re-configuration activities to the existing GCC- SCADA system resulting from new facilities and required to make a whole project function

The Contractor shall be responsible to transferring the data via Ethernet as a master and provide a V-24 data transferring as a slave.

11.3	TESTING, COMMISSIONING AND START-UP:

11.3.1	Testing:

CONTRACTOR shall supply all necessary equipment and labour required for testing. Testing shall be done in the presence of the COMPANY's representative and the applicable inspection authority.

Testing on the Control of FMS including Compressor units, Metering and Communication Systems shall be in accordance with Specifications.

All results of tests and readings shall be recorded, certified and issued to the COMPANY.

11.3.2 Commissioning and Start-up:

The CONTRACTOR shall provide sufficient manpower for the duration of the commissioning and start-up period. CONTRACTOR shall be aware that the commissioning period is the time required to check wiring and control systems and make corrections as required making the system READY FOR START-UP. The start-up period is the time after commissioning to put the Project into continuous operation.

CONTRACTOR shall accept the direction and advice of the COMPANY’s representative in all areas of commissioning.

11.4	FIELD INSPECTION:

Inspection activities shall be performed as specified in the exhibit B section 1- General Scope and Definitions, par. 1.1.5-Inspection.

Inspection shall not relieve CONTRACTOR from any duties, obligations, responsibilities or liabilities under the Construction Agreement

11.5	DRAWINGS:

All Drawings in this section shall be supplied by the CONTRACTOR as per AFPC Schedule-B, Engineering Documentation.

11.5.1 DRAWINGS:

Contractor shall provide all drawings for all activities of project.

Contractor shall keep a set of construction drawings which they will mark-up reflecting the As-Built Installations and shall submit such drawings red marked to the COMPANY within seven (7) days of job completion as well as, the final “As Built” drawings in both   hard and soft copy to be delivered to COMPANY within one month from the date of issuing of Mechanical Completion Certificate (MCC).

By "As-Built", it means that the Contractor has adequately shown, or provided additional sketches, to clearly convey the information for the actual pipeline, piping, electrical and instrumentation configuration etc.

Additionally, all as built drawings, configuration, programming and application software shall be bucked-up and provided on DVD (2 copies).

Company shall supply some drawings for information.

11.6	CONTROL EQUIPMENT SPECIFICATIONS LIST

All Specifications lists for the Control, Metering and Telecommunication Systems - shall be supplied by the CONTRACTOR as per Schedule-B, Engineering Documentation.