Table of Content

1	Abbreviations	4

2	Introduction & scope	5

3	Applicable Codes and Guidelines	5

4	Overall System Requirements	5

4.1	General	5

4.1.1	Year 2000 compliance	6

4.2	Redundancy of DCS Equipment	6

4.2.1	Item Redundancy	6

4.2.2	Redundant Part Replacement	7

4.3	System functional Requirements	7

4.3.1	Control System Functional Requirements	7

4.3.2	Steady State and Dynamic Control	7

4.3.3	Sequence Control	7

4.3.4	Advanced Control	8

4.3.5	On/Off Switching	8

4.3.6	Control loop scanning rates	8

4.3.7	Workstation Normal Functions	8

4.3.8	Access Security	8

4.3.8.1	Operator Level	8

4.3.8.2	Engineer Level	8

4.3.8.3	Supervisors Level	9

4.3.8.4	View Only	9

4.3.9	Data Storage Systems	9

4.3.10	Printing	9

5	Spare capacity requirements	9

5.1	Hot Spares	9

6	System Hardware Requirements	10

6.1	Console Facilities	10

6.2	Printers	10

6.2.1	Alarm/Event printer	10

6.2.2	‘Other’ printer	10

6.3	Processors	10

6.4	Resident Memory	11

6.5	Operator Workstation	11

6.6	Engineering Workstation	11

6.7	Network Configuration	11

6.7.1	Time Synchronisation	12

6.8	Termination of Field wiring, DCS Cabinets	12

6.9	Power Supplies	12

6.10	Allocation of Racks and Equipment Cabinets	13

7	Software Requirements	13

7.1	Configuration	13

7.1.1	On-Line Configuration	13

7.1.2	Off-Line Configuration	13

7.2	Data Base Management	13

7.2.1	General	13

7.2.2	Tag Number Configuration	14

7.2.3	Storage/Back-up	14

8	Interfacing	14

8.1	General	14

8.2	Plant interfaces	14

8.2.1	Standard Process I/O	14

8.2.2	Motor Control Interface	15

8.2.3	Interface with ‘Foreign Devices’.	15

8.2.4	Safeguarding System Interface	15

9	Displays	15

9.1	General:	15

9.1.1	Performance	16

9.2	Display structure	17

9.3	Display configuration	18

9.3.1	Symbols	18

9.3.1.1	Symbol usage	18

9.3.1.2	Symbol size	18

9.3.2	Typical symbols, colours and status display	18

9.3.2.1	Process lines and process equipment	18

9.3.2.2	Valves	18

9.3.2.3	Rotating equipment (pumps, , motors etc.)	19

9.3.2.4	Instrument signal lines	19

9.3.3	Use of colours	19

9.3.4	Highlighting	20

9.3.5	Blinking and colour change	21

9.3.6	Brightness	21

9.3.7	Inverse (reverse) video	21

9.3.8	Process data representation	21

9.3.8.1	Numeric data point	21

9.3.8.2	Bar display	22

9.3.8.3	Short duration trends	22

9.3.9	Controller parameters displayed in graphics	22

9.3.10	Labelling	22

9.3.11	Text	23

9.3.12	Tables	23

9.3.13	Windows	23

10	Alarms/Events	24

10.1	Alarm philosophy	24

10.2	Alarm Management	24

10.2.1	Alarm Masking, Inhibit and Disable	24

10.2.2	Alarm Handling	25

10.2.3	Alarm Acceptance	25

10.2.4	Audible Alarms	25

10.2.5	Alarm resolution	26

10.2.6	System Response	26

10.2.7	Alarm and Event Logging	26

11	Transmitter Validation	26

12	Trending/Reporting	26

12.1	Trend archives	27

12.2	Real Time Trends	27

12.3	Tuning Trend	27

12.4	Historic trends	27

12.5	Reporting	27

13	Earthing	27

14	System Availability	28

15	System Maintainability	28

16	System Immunity	29

17	Warranty Period	29

18	PROJECT REQUIREMENTS	29

18.1	Functional Design Specification	29

18.2	Commissioning	30

18.2.1	Pre-Commissioning	30

18.2.2	Final Commissioning,  including plant start-up.	30

19	FACTORY ACCEPTANCE TEST (FAT)	31

19.1	General	31

19.2	FAT phase 1	31

19.3	FAT phase 2; System Integration Test (SIT)	32

19.4	Operational Support	32

19.5	Field Support	32

19.5.1	Remote Diagnostic Service	32

19.6	Spare parts	32

19.7	Documentation	33

19.8	Manuals	33

19.8.1	Operating manual	33

19.8.2	System manual	33

19.8.3	Maintenance manual	34

19.8.4	Drawings	34

20	Training	34

# Abbreviations

| APC | Advanced Process Control |
| --- | --- |
| CCTV | Closed-Circuit Television |
| CPU | Central Processing Unit |
| CRT | Cathode Ray Tube |
| DCS | Distributed Control System |
| ESD | Emergency Shutdown |
| FAT | Factory Acceptance and Testing |
| FGS | Fire, Gas and Smoke detection and protection system |
| GPS | Global Positioning System |
| MOS | Maintenance Override Switch |
| MTBF | Mean Time Between Failure |
| MTTR | Mean Time To Repair |
| MVC | Measurement, Validation and Comparison |
| PV | Process Value (process parameter being measured) |
| QMI | Quality Measuring instrument |
| SAT | Site Acceptance Testing |
| SAT | Site Acceptance and Testing |
| SCADA | Supervisory Control And Data Acquisi |
| SER | Sequence of Events Recorder |
| SGS | Safe Guarding System |
| SIT | System Integration Test |
| SP | Set-point |
| SQL | Structured Query Language |
| UCP | Unit Control Panel |
| UPS | Un-interrupted Power Supply |
| VDU | Video Display Unit |

# 2	Introduction & scope

This specification defines the basic functional and technical requirements for the design, engineering, testing and commissioning of a Distribution Control System (DCS) for an SGC facility in Syria.

This specification shall be used for new DCS systems.

In case of extensions or expansions of existing DCS, a more specific specification needs to be developed to cover the required extensions.

The DCS vendor may assist in establishing the hardware requirements in those cases.

The Distributed Control System shall be a microprocessor-based system, which shall carry out real time control and monitoring of the production facility and interface with the facility’s electronic measuring instruments and actuating devices.

The Contractor/vendor shall expand this functional specification during detailed engineering phases into a ‘Functional Design Specification’, specific for the project.

The offered DCS under this specification might have other functions or alternatives, which may reduce Total Cost of Ownership (TCOO). These should be brought to the attention of SGC (in addition to the ‘base bid’ requirements), clearly stating the variations and advantages from the specified requirements.

The DCS shall be interfaced with other systems to provide the operator with all essential information of the total process, including, process safeguarding monitoring, F&G status monitoring, etc., irrespective the source of the information (one window interface concept).

Where (parts off) a DCS is supplied as an integral part of a package unit, they shall also comply with the requirements, where applicable, contained herein.

# Applicable Codes and Guidelines

The following Codes and standards are applicable to the DCS

	BS 6667
 Method of evaluation of susceptibility to radiation of electromagnetic energy.

	BS 6527
 Limits and methods of measurement of radio interference characteristics of information technology equipment

	MIL-STD-HDBK-2 17E
 Reliability prediction for electronic equipment

	ISO 9001-4
 Quality Systems. Relevant parts.

	IEC 801 Electromagnetic compatibility for industrial process measurement and control equipment

	IEC 1000-5 Electromagnetic Compatibility (EMC) part 5

	IEC 617-12 Graphic symbols for diagrams, part 12

- AFPC schedules:

	L-2 Instrumented Safeguarding Systems

	L-5 Instrument Signal Lines

# Overall System Requirements

## General

The DCS shall be supplied fully configured comprising of all hardware and software necessary to meet the functional requirements specified, ready for use when connected to equipment sensors and actuators in the facility.

In case of an extension of an existing system, Contractor shall ensure that overall system integrity is ensured and that the proper functioning of the existing systems is not adversely affected by the extension, nor during the implementation of the extension.

All proposed DCS equipment and software should be of proven (high) reliability and utilise standard software and hardware.

The system software shall be of the latest proven international release at the time of Factory acceptance testing (FAT).

In case of an extension of an existing DCS, the system software release shall be that of the existing parts, unless the applied (new) hardware or software requires an upgrade. In that case all DCS's on site having the same release, shall be upgraded.

The DCS shall be designed, constructed, factory tested, installed and re-tested on site to ensure its correct functioning as an integrated system. SGC reserves the right to attend all factory acceptance tests.

The DCS vendor shall ensure that overall DCS system integrity is maintained and data communication between the various nodes and sub-systems are not overloaded. DCS equipment shall be located in a (control) building.

The DCS shall be designed with in-built flexibility for future expansion. This expansion shall be achieved by the straightforward addition of hardware, on-line and under full power, without impacting the current DCS operation. Requirements for software and configuration changes for the addition of hardware shall be minimised.

The Vendor shall specify the maximum future expansion capabilities of the proposed DCS.

The DCS shall not suffer any adverse performance effects, when it is loaded to its maximum capacity in terms of hardware and software. The Vendor shall present the expected load if the full "spares" allocation + 20% were required in the future and what, if any, additional equipment/configuration changes would be required.

### Year 2000 compliance

The system including all products and services supplied by sub-vendors shall be Year 2000 compliant, i.e.: The system will continue to function and its functionality and accuracy (both logical and mathematical) will not be affected as a result of the run date or the dates being processed, irrespective of which century the dates fall in, and the product recognises the year 2000 as a leap year and accepts 29th February 2000 as a valid date.

## Redundancy of DCS Equipment

### Item Redundancy

The following redundancy requirements shall be applied:

Item
Communication-, Control Network, Field bus		Redundant 
Controller/application processor		Redundant
	Input and output cards for control functions 		Redundant for critical loops, otherwise Single.

Input and output cards for monitoring only 		Single
Process interface/field bus modules		Redundant
VDU electronics + keyboard		Dual 
Power supply 		Redundant 
Gateways to SGS/F&G incl. link		Redundant
Gateways to other systems		Single/Redundant (depending on criticality of application).
Alarm Printers		Single, shared with report printers.

Report Printers		Single, shared with alarm printers.

Floppy /DVD drivers.		Dual 
Hard disks for mass storage		Redundant (volume shadowing).

### Redundant Part Replacement

For items having a redundant unit, it shall be possible to replace, test and restore the failed unit without disrupting the functionality of the DCS including subsystems.

There shall be no need for operator intervention to re-enter data or reload programs following a power supply- or component failure. Upon manual reset, the DCS (or component) shall automatically come on-line.

The consistency of the database, integrity of the data and the continuity of control loops shall be maintained during re-initialisation.

## System functional Requirements

The objective of this section is to specify the configurable software functions, which must be supported by the DCS.

### Control System Functional Requirements

In order to provide the operator with the tools necessary for reliable and proper facility control, the DCS shall contain at least the following functions:

	Sequence Control
	Steady State and Dynamic Control
	Advanced Control
	Advisory functions
	Process Data Collection. 
	On/Off Switching
	Alarm & Event Generation/Handling
	Graphic Displays 
	Group Displays 
	Loop Displays 
	Alarm Summary Displays 
	Trending (real time and historical)
	System Diagnostics 
	Computational functions
	Logging and reporting functions
	Interfacing with other systems, e.g. SGS, FGS, UCP, SCADA
	Run application programs

### Steady State and Dynamic Control

The DCS shall be designed for steady state plant control between the maximum and minimum design conditions as specified in the basis for design.

As far as practicable the DCS shall be designed in such a way that the effect of operational variations and disturbances in one section of the plant will have a minimum effect on other sections.

All control functions required for normal feedback control (PID), ratio control, master slave control etc. shall be implemented in configurable modules, with selectable auto tuning features, within the DCS. No components of closed loop control are allowed to be implemented in special or dedicated hardware ‘boxes’ outside the DCS.

Other functions required for non-closed loop control, e.g. as required to facilitate start-up or mode switching, may be implemented in free programmable- or computational modules in the DCS.

All split range control for the control valves shall be implemented in software within the DCS.

### Sequence Control

The sequence control system should normally operate fully automatic without the operator attention. A manual mode of operation should be made available in order to cope with abnormal conditions. 
A mimic picture should be provided on the DCS VDU in order to show the status of valves and the controller. Valves for sequence control functions shall be provided with reliable position indicators as needed for sequence control action confirmation and valve interlocking.

### Advanced Control

The DCS shall include a ‘Measurement, Validation and Comparison’ (MVC) function and other advanced control functions specified in the contract.

### On/Off Switching

On/off switching (e.g. for equipment, automatic cut-in of a spare pump in case of failure of the primary one) is considered to be 'control' rather than 'safeguarding or emergency shutdown' and shall be implemented in the DCS.

### Control loop scanning rates

Control algorithms shall be executed with a scan period of 0.5 second. For a minimum of 10% of the total number of control loops a faster scan period of 0.1 second shall be possible.

### Workstation Normal Functions

The operator workstation shall be the main interface with the plant. All process information shall be displayed via the DCS. As a minimum it shall provide:

	Operator displays and control functions 
	Alarm / event handling, display and logging 
	Real time and historic trending
	Operational procedures

### Access Security

To prevent unauthorised access to databases and configuration data the system must support several levels of access under password or key-lock control.

Access levels shall include, but not be limited to:

	Operator level
	Engineer level
	Supervisor Level
	View only

It shall be possible to enter each level of access at any operator workstation. The access level shall be entered for an individual workstation without changing the access level of the other workstation(s).

#### Operator Level

Operator level shall permit normal operator access for:

	Loop manipulation 
	Start/Stop, open/close functions 
	Alarm acknowledgement & reset
	Call up of all operator displays 
	Trend selection 
	Alarm printout facilities, Historical printouts 
	Reports

#### Engineer Level

Engineer level shall permit access to Operator functions as above and additionally give access to:

	Database facilities for editing, generation and back up of both global and area databases
	Loop configuration and tuning facilities 
	Display building facilities 
	Programmable functions 
	System network and node diagnostics facilities 
	Generation of logs and reports

#### Supervisors Level

Supervisor shall have access for all the functions listed for the operator level. Additionally the supervisor shall have access to loop tuning parameters, process ranges, operator alarm settings etc. 
The supervisors console shall be capable of accessing all information from all operators consoles.

#### View Only

The process may be viewed, while data entry or process changes are not possible.

### Data Storage Systems

Data storage systems will be used for: 
	System software back-up 
	Historical Data/events recording 
	Storage of system database and configuration

- Printing

The system shall provide facilities for printout of:

	The system database configuration and programs
	VDU displays
	Custom Historic trends of process and calculated variables
	Real time trends of selected variables
	Alarms
	Event logging, including operator keyboard actions.
	Process parameter deviations from their set point (or target)
	Trip alarms, MOS actions (these are also printed via the SER in SGS).
	Reports
	System diagnostics

# Spare capacity requirements

The DCS, after commissioning, shall include the following spare capacity:

10%	installed, pre-wired, spare I/O cards, with a minimum of one of each type used in the DCS.
20%	wiring, terminals, power capacity, spare space/slots in I/O racks etc. for future expansion.
40%	spare memory, disk space, processing and data highway/network capacity.

## Hot Spares

Hot spares shall be mounted, powered and active in the DCS and subject to standard DCS diagnostic routines ready for plug in replacement of failed components. Replacement shall be possible without powering down or otherwise compromising normal plant operation.

The hot spares inventory shall include at least one I/O card of each type and other components, which are not redundant, but whose failure would degrade DCS performance. The spare hardware listed above may be used to fulfil the hot spare requirement.

VENDOR shall specify the installed spare hardware and the spare space in the cabinet in his proposal.

# System Hardware Requirements

## Console Facilities

If a new console is required, the console shall comprise of workstations, i.e. VDU's and keyboards, pointing device together with: 
	Printers 
	Communication facilities, if specified
	Sequence of Event Recorder

Pointing devices like tracker balls, mouse or joystick for cursor control will be given preference over keyboard control only. A desk top type operator interface, whereby the VDU, keyboard and pointing device are supplied as separate items and are placed on tables to form a console is preferred. 
The arrangement of the furniture can be customised to the requirements of the users (e.g. two tier or single tier VDU holders). The console shall have sufficient writing space.

Console support electronics, including communication systems, should preferably be mounted in the Console.

## Printers

As minimum two printers are required, one ink-jet for alarm/event- and one Laser for ‘other’ printing purpose. Both shall be of printers, requiring minimum maintenance and which are noises free (less then 55-dB (A) at 1 metre while printing). They shall be fitted with printer cartridge(s) and integrated paper feed box and paper catcher. Minimum line length shall be 132 characters
The printer shall have self-contained test and diagnostics to aid in trouble shooting.

The output to the printer shall be buffered.

The operator shall be able to direct logs, reports, system configuration/listing/diagnostics etc. to either printer.

Alarm/Event printer

Logging of new alarms shall be in red colour and ‘alarm return to normal’ shall be printed in black. Through a ‘soft switch function’ in the DCS, it shall be possible to switch off automatic Alarm/Event printing, however it shall be possible to select an arbitrary time block, where alarms/events within this selected period, shall be printed only.

### ‘Other’ printer

This printer shall be a full colour graphics printer to enable:

-	Screen dumps of any display 
- Print of trends 
- Print of logs/reports 
- Print Alarms/Events re-directed from alarm/event printer
- Print of system configuration/listing/diagnostics

## Processors

The System processors shall execute application/control software, operator actions and shall have the following features:

	Power failure protection
	Automatic restart facilities 
	Memory protection 
	RAM stack overflow detection 
	System synchronised Real time clock 
	Watchdog timer 
	Hardware diagnostics
	Operating system automatic start-up

## Resident Memory

RAM memory shall have battery back up to protect against loss of memory on power failure or voltage depression.  Batteries shall be of leak-proof design. The battery hold-up duration shall be 30 minutes and shall be automatically recharged when power returns to normal or, in case of non-rechargeable batteries, their lifetime shall be at least 5 years.

## Operator Workstation

For displaying graphic symbols, high resolution VDUs should be used which can reproduce at least 1024 x 1024 pixels or 1280 x 1024 pixels with a minimum screen size of 19 inches.

To avoid flicker, image refresh frequency should be 70 Hz for displays using dark symbols on light backgrounds.
Contrast and brightness should be adjustable.

Monitors shall be manufacturers standard and support ‘Windowing’techniques.

The windowing capability shall among other possibilities allow the operator to view multiple group displays (typically 4), graphic displays etc. on one screen. This will greatly enhance the 'parallel' view of the operator on the process and increase the number of 'virtual' screens.

The keyboard shall be of (spill proof) Miler membrane type and support customised key functions.

When specified the VDU electronics shall be equipped with 'Video in Windows' capabilities, i.e. a video signal received from a CCTV system is to be connected to the workstation electronics and the operator may view the CCTV picture in a sizeable window. Others will provide the actual CCTV system and signal cable. The signal will be PAL.

It shall be possible to use the operator workstation also as an ‘Engineering workstation’ with the functionality specified below.

## Engineering Workstation

When specified, an additional, dedicated, engineering workstation with a VDU, ‘QWERTY’ type keyboard and a printer shall be provided, to be located in the Engineer’s office or in the control room. The Engineering workstation will be used for all database configuration and generation, upload / download of data to system nodes, report building, system analysis and diagnostics etc.

The workstation shall include floppy and DVD drives to ease data back up and storage.

## Network Configuration

The DCS shall include a fully tested high-speed network, which will control all communications between consoles, nodes etc. The communication networks shall be fully redundant including the communication interfaces for each device on the bus.

The redundancy in communication buses shall be active in nature, i.e. both the busses shall be active and shall periodically switch over at a pre-determined frequency. It shall be possible to manually switch the busses from the operator interfaces.

In case of failure of one of the busses, the other bus shall take over automatically without any interruption to the process and with a diagnostic alarm informing the operator of the failed bus. 

Nodes shall communicate with each other in such a way that the source of data is transparent.

It shall be possible to add nodes, e.g. workstations, interfaces, host computers, controllers etc., to the existing busses without affecting the current communication. These new nodes shall then be capable of being configured on-line without impacting the current DCS operation.

The DCS shall be capable of being expanded by linking multiple networks together for a plant wide integrated DCS. Multiple networks shall be accommodated when unit separation and isolation are desired. The separation and isolation shall be accomplished by ‘Network Gateways’ which will allow the transfer of data from one network to the other while maintaining the security of each independent network. The ‘Network Gateways’ shall communicate via the ‘IEEE 802’ protocol.

When multiple networks are implemented via a ‘Network Gateway’, a security access mechanism shall be utilised to allow / limit data transfer.

The access levels shall be:

-	Read only access
-	Read and Write access
-	No access

Each individual network shall support and allow for independent, stand alone, loading and operation.

### Time Synchronisation

Time synchronisation shall be employed to ensure strict co-ordination between modules. 
Individual clocks in DCS modules and clocks of sub-vendor equipment (connected by serial link), shall always agree within 10 millisecond of the main DCS clock. The Vendor shall advise by which means this will be achieved. Drifting of actual real time shall be no more than three (3) seconds.
The DCS shall provide the facility for the operator to input system date and time via the operator interface. All DCS facilities shall be synchronised to this system time and date which shall be used for time-tagging all alarm and events and in all displays and reports. If time synchronisation is required across different sites (i.e. independent DCS’s) then GPS time synchronisation should be considered.

## Termination of Field wiring, DCS Cabinets

The DCS shall be provided with all necessary termination/marshalling and system cabinets with all associated accessories, racks, wiring, terminals blocks and intrinsically safe barriers (when required they shall be fitted in the marshalling cabinets). For details refer to schedule L-5 ‘ Instrument Signal lines’.
The signals to and from the marshalling racks shall be connected in a systematic way to the control units and the process interface units such that a clear, and therefore easy to maintain arrangement, is achieved, even if this means unused I/O channels. These unused channels may be included in the calculation of the spare capacity per block.

To reduce cost field termination assemblies may be installed in the marshalling cabinets in order to limit the number of connections and cable terminations within one loop and to limit the DCS cabinet space required.

## Power Supplies

The DCS shall be powered by 220-240V AC 50HZ (+- 5%) and/or 24 V DC (+-10%) supply

The power supply shall be from two different sources, i.e. one main and one backup. Each power supply is allowed to fail (or be isolated, e.g. for maintenance) without giving rise to loss of control, I/O monitoring, alarming and the ability for the operator to view and manipulate the process. 
The backup power supply shall be sized for at least 30 minutes prolonged operation, including ancillaries such as printers, VDU etc.

Each supply shall be designed such that it will carry no more than 75% of the capacity under normal loads.

Power supply distribution shall be segregated in process units to allow unit wise maintenance and shutdown.

Power packs shall be included for powering system components and process transmitter and converters at 24 volt DC. The DCS system shall include 24V DC power for digital inputs and outputs.

Individual loop fusing shall be provided.

The system shall include for double pole isolators and over current protection for all incoming supplies. Sufficient isolation facilities on the DC subsystems shall be provided to enable maintenance and replacement of components with minimum disturbance.

Work stations and peripherals shall have internal over current and isolation facilities.

## Allocation of Racks and Equipment Cabinets

Where feasible, DCS modules shall be allocated to process units such that failure or maintenance of such a module only affects the allocated unit.

Cabinets shall be manufacturers standard equipped with plinths and doors with key-lock. In absence of a manufacturers standard, Rittal PS4806 cabinets are preferred with 180o hinged double doors

# Software Requirements

The DCS shall be designed and configured with all software necessary to fulfil the functionality- and maintainability requirements specified.

The DCS shall include standard software packages, operating system and application software, including diagnostics and communication software.

New operating system software releases shall be downloaded on-line without upsetting plant control.

## Configuration

### On-Line Configuration

It shall be possible to re-configure any particular control-loop on-line, without disrupting any other control-loop in the DCS.

Data-entry type checking shall be incorporated into the DCS to prevent entry of invalid data. e.g. alpha versus numeric, etc.

### Off-Line Configuration

Configuration and display software shall be able to be run on an IBM compatible PC.  This will allow configuration and graphics building before DCS hardware becomes available. The Vendor shall specify the hardware and software requirements for such a PC system. It shall be possible to create advanced control schemes from this PC.

## Data Base Management

### General

The database shall hold point definitions for all physical, derived and pseudo inputs and outputs. The DCS shall allow the operator to examine all information pertaining to any tag number in the DCS.
System shall support relational database access techniques (SQL)

It shall be possible for the engineer to amend, add or delete any point in the DCS database, while the DCS is operational, in a simple "fill in the blanks" manner under security access. All changes to the database are to be checked and verified during entry. Control loop integrity shall be maintained against inadvertent engineer action e.g. deletion when the loop is in automatic mode.

Simultaneous configuration of the same data shall not be possible. All accepted definitions and subsequent changes shall be saved by the appropriate module(s).

### Tag Number Configuration

A single unique tag number will be assigned to each variable and its associated control function. A tag number shall consist of sixteen (16) characters as a minimum (e.g. TAN-LICA-1021-A) excluding identifiers required by the Vendor to name points or blocks in a loop. In addition a minimum of 32 characters shall be fully assignable to each tag as a point descriptor and each point shall be assignable with six (6) engineering units, the sequence of alpha and numeric characters shall not be restricted by the DCS in any way and (tag number) descriptions shall be user configurable. All characters shall be displayed / reported.

### Storage/Back-up

It is required that the DCS maintains, on mass storage media, the complete current database. Any changes made to the database shall also be copied to mass storage.

Therefore the DCS shall be equipped with:

- a)	Fault tolerant non-removable hard disks, minimum size 80 Gbyte, containing all system

Software, application software, displays, logs, historical trends and data files (sized as defined in this document) etc.

- b)	Removable mass storage media e.g. Bernoulli or optical DVD\RW drive, for initial DCS

Loading and long term storage of historical data and system software back-up.

- c)	3 1/2” floppy drive for interfacing with IBM compatible PC.

If a memory loss occurs then the DCS shall allow reloading with either an archived or the current back-up version of the database from the mass storage media. The DCS shall allow the database of any outstation to be saved or loaded to / from back up individually.

The data storage operation shall not require specialised personnel nor degrade the performance of the fully operational DCS.

# Interfacing

## General

The DCS shall have interfaces to other related systems such as Safeguarding Systems, CAO/SCADA and Equipment Packages.

Automatic protection and interlocking functions for safety purposes shall not be executed in the DCS, however in a separate stand-alone (SGS) system.

Note: Instrument Safeguarding System shall have their own initiating devices (transmitters etc.) and actuating devices. (Refer to schedule L-2 ‘Instrumented safeguarding system)

## Plant interfaces

The physical interface to plant sensors and actuators shall be via hardwired I/O. 
The I/O equipment shall be located in the control building/Instrument auxiliary room.

### Standard Process I/O

The DCS shall accept the standard range of field I/O.

Intrinsically safe barriers ‘active’ type shall protect I/O modules, where required, or galvanically isolated.

The DCS shall provide 24V DC power for the transmitters in the process units. It is also possible that other equipment will provide power for the 4-20mA signal. It shall be possible to locate the I/O sub-system remotely, i.e. away from the control sub-system.

Where feasible the I/O shall be functionally segregated such that a single (non-redundant) component failure only affects one piece of equipment or one section of the facility, while the rest of the facility remains operational.

I/O allocation shall therefore be on the same basis as the safeguarding ‘SD’ group allocation to ensure proper segregation / separation of equipment.

For non-redundant I/O items, the I/O shall "freeze" on the last signal or go to a "fail-safe" position. This shall however be configurable on a per output basis. Digital field communication shall not be used until the ‘Fieldbus’ development is sufficiently mature, internationally recognised and used. Only when digital communication is specifically mentioned in the Contract, shall it be considered

### Motor Control Interface

The DCS shall provide for start/stop commands and indication of motor running status and mode (as specified on the P&IDs).  The start/stop commands will be transmitted  (by serial link) via the SGS to the MCC via the IRP (refer to schedule L-2). Running status and mode information may also be transmitted to the DCS by serial link, in case of use is made of ‘intelligent’ switchgear, otherwise 24 V DC digital input, powered from DCS, shall be provided.

### Interface with ‘Foreign Devices’.

The DCS shall be able to interface with ‘foreign devices’ via serial links using the Modbus RTU protocol or other internationally recognised, superior communication standard like ETHERNET. The DCS shall act as the communication ‘master’. The links shall be self-starting and the communication protocol shall incorporate error detection capabilities.

The DCS shall check for message transmission and structural errors. Link failure shall in no way affect the integrity and normal continuation of plant control.

Where supported by the foreign device protocol, the link shall support transfer of time stamping and clock synchronisation.

The DCS Vendor shall assume total responsibility for the serial communication link. He shall liase with the foreign device vendors or suppliers for the necessary details to design/configure the link, i.e. register assignment, protocol, data transfer format. The link shall be fully tested with the third party equipment.

All hardware and software required in the DCS and interconnecting cabling between the foreign devices and the DCS shall be in the scope of the DCS Vendor.

Serial link scanning rates shall be 0.5 sec. or faster.

Each serial link shall at least have 20 % installed spare capacity.

### Safeguarding System Interface

Data shall be provided from the SGS for display/printing/logging in the DCS.
 The communication link to the safeguarding systems shall not carry ‘safety related ‘ signals.
Also a number of commands (resets, MOS requests, start/stop) shall be transmitted to the SGS from the DCS. Refer to schedule L-2.

# Displays

## General:

Graphic displays should be logically built up based on P&IDs showing details of process equipment ( vessels, columns, pumps, etc.), process flow and relevant control loops. Dynamic data for process variables, alarms and equipment status should be  incorporated in the schematics to provide a realistic appreciation of plant operation. The graphics shall help the operator to visualise the process so as to enable him to perform his task effectively.

Graphics may also take the form of specific displays such as tables showing switches, APC displays, plot plans and sequence displays to provide reference information to the operator. It shall be possible to display also Cause and Effect diagrams (refer to schedule L-2)

A minimum of 200 freely configurable displays per workstation should be possible.

Each display shall consist of real time data points to allow adequate process control using these graphics without being too congested or otherwise confusing. The displays should not be cluttered since excessive information may result in extended search times by the operator and a loss of clear direction. There should be no more than 40 live data points per display.

Graphics should be oriented from left to right with pipes or signal lines entering from the left and leaving at the right. Crossing pipes or signal lines and details not needed for the understanding of information should be avoided as much as possible.

Process equipment that cannot be controlled (e.g. isolation and bypass valves) should not be shown unless this information is needed for a proper understanding of the task.

The main criterion for depicting information should be task driven for the major equipment displayed, e.g. a graphic for the control of a furnace should contain all control aspects including combustion control.

The outer edges of the displays may be obscured by the rim of the CRT if the operator is not sitting directly in front of it. Therefore this area should not be used for data display.

Screens should be organised in such a way that the user can almost "naturally" go from one screen area to another. The flow of information should be from left to right, and from top to bottom.

Each workstation shall include a menu of all displays available at the workstation.

The display access methods used shall permit movement between display hierarchy levels by mouse/trackball and keyboard with a minimum number of ‘key-clicks’.

### Performance

Static graphic displays shall be fully displayed on the VDU within two seconds from the operator's call-up request.

Graphic displays with dynamic data shall be fully displayed on the VDU within four seconds from the operator's request.

With a display in view, dynamic points shall be updated within 2 seconds from the change of state or change of value.

## Display structure

A structured approach of graphics types shall be applied to present plant information to the operator. The hierarchy of graphics that should be configured in the DCS is given below.

- Typical DCS display hierarchy

## Display configuration

Unless otherwise specified the conventions indicated below shall be used.

Note: For extensions/modifications to/of existing DCS displays, the existing display convention shall be applied.

### Symbols

Symbols within graphics should be used to represent specific plant items and thus assist in plant item identification. They may also be used in conjunction with other methods, e.g. colour, to indicate changes of plant item state.

#### Symbol usage

Graphic symbols shall be arranged to depict physical relationships, and shall flow in a consistent manner, i.e. from left to right, from top to bottom. Arrows should be used in process lines to indicate direction of flow. Symbols should only be shown if they are important for the understanding of the operations or if they are an integral part of the process depicted. Symbol qualities (e.g. contrast, luminance) shall be used judiciously to avoid any masking of adjacent display targets.

A symbol library should be compiled and used in the process schemes. These symbols should be based on internationally used conventions e.g. P&ID symbols. They should be developed and stored in the graphic library for generating the graphics. Where applicable, minimum size and associated attributes should be specified (example: closed valve: hollow, open valve: filled).

#### Symbol size

As a general rule a symbol (considered square or circular) should be at least 5.0 to 6.0 mm in height. This makes the symbol easily distinguishable from a distance of 1 m.

The label identifying the symbol should be positioned in such a way that it is clear, which symbol and identifier belong together. There should be consistency in positioning the label location relative to the symbol (e.g. underneath the pump). Vertically oriented labels should be avoided.

### Typical symbols, colours and status display

The following convention should be used:

#### Process lines and process equipment

Lines with a typical width as indicated below should be used:

Main process lines:	3-dot width,

Minor and utility process lines:	2-dot width

Process equipment:	4-dot width

The following line colours for process lines should be used:
Gas: yellow; - Oil: green; - Water; blue. - Other: white, unless otherwise advised.

Crossing lines should be drawn such that the vertical line breaks at the crossing point. This should be used consistently in all graphic displays.

#### Valves

Monitored valves should be presented in white. A single valve symbol may be used to represent all types of valves.

| Open | line colour white, filled |
| --- | --- |
| Closed | line colour white, hollow |
| Travelling | line colour white, inverse video (On/Off Service) |
| Bad value | Magenta (Fail to travel) |

#### Rotating equipment (pumps, motors etc.)

| Running | line colour white, filled |
| --- | --- |
| Off (available) | line colour white, hollow |
| Bad value | perimeter Magenta |
| Tripped/Alarm | Red, blinking, alternating hollow and filled, tag red until acknowledged |

#### Instrument signal lines

Representation of instrument lines is generally applied at the (sub) unit and detailed display level. Instrument lines should not be shown at plant overview level.

Instrument lines should be white dashed lines (1-dot width) to distinguish them from process lines. They are used to support understanding of the control schemes (i.e. showing which valve a controller control). Switched control lines shall be shown dynamically.

Whenever instrument lines are shown on a graphic, these should be given to a target, which will toggle these lines on / off, thereby the number of items displayed on the screen. This can be achieved by using the inverse video feature.

### Use of colours

To avoid the problems and ambiguities in applied colour conventions (colour should not be the sole means of distinguishing important plant items and states)

the colours used in the display should be:

| Foreground colours: | Red, yellow, green, cyan, magenta, white |
| --- | --- |
| Background colours: | Light grey or dark grey |

The colours given below together with their usage should be applied.

| COLOUR | USAGE |
| --- | --- |
| Red | High priority alarm indication (primary alarms and SD alarms); |
|  | Alarm text in alarm banner and in alarm list display |
|  | Equipment with tripped/alarm status; |
|  | Trend line in trend display. |
| Yellow | Trend line in trend display |
| Green | Healthy logic signal; |
|  | Fire and gas displays showing normal status; |
|  | Trend line in trend display. |
| Cyan | Trend line in trend display. |
| Magenta | Unreliable data indication in process scheme displays; |
|  | Equipment giving readings known to be faulty; |
|  | Unreliable data point in process scheme; |
|  | Fault status in fire and gas displays; |
|  | Trend line in trend displays. |
| White | Text, labels, numeric data in normal intensity; |
|  | Electrical distribution lines, signal lines; |
|  | Normal status indication of equipment (open valves, running rotating machinery, circuit breaker in make state); |
|  | Inverse video white for manually entered data; |
|  | Touch target borders, half line thickness; Touch target legends |
|  | Framing lines in bar graph and trend displays, in block diagram displays and in instrument lines |
|  | Background grid in trend displays, half line thickness. |
| Grey | Background colour of the screen for all displays, except for: |
|  | the background for the trend- and bar graph displays and the background of displays |
|  | Windowed into other displays. For these a black background should be used. |

- The following colour conventions should be avoided:

Pure blue

Pure blue on a dark background should be avoided for text, thin lines or high-resolution information.

Chromostereopsis
Simultaneous presentation of both pure red and pure blue (or to a lesser extent red and green, or blue and green) on a dark background may result in chromostereopsis (a three-dimensional effect) and should therefore be avoided.

Pure red

Dominant wavelengths above pure red should be avoided in displays.

Background colour

Coloured (white or chromatic) information should not be used against a background, which is black and has no apparent visual texture. This produces an excessive contrast between the background and the characters so that the latter may have a tendency to appear to float in space and appear at different visual distances. Also, if the background is very light it may be impossible to provide sufficient brightness for the (foreground) information to satisfy contrast requirements. It is recommended to apply a greyish background that remains neutral in colour under the ambient light and looks like a surface on which the information is placed.

### Highlighting

Highlighting should be used as a means of emphasising some items in the display, such as label, data item, title or message. It should be used in moderation to be effective. Excessive use of highlighting will be self-defeating as "contrast" with the surroundings is reduced. The recommended methods of highlighting are indicated below.

NOTE:	Underlining, fonts, upper case letters, double-size characters, thin/thick/double rulings should not be used for highlighting purposes because they are not very effective in drawing attention.

### Blinking and colour change

Blinking and colour changes should be used to attract the attention of the operator (e.g. normal or healthy condition: green, alarm condition: red).

Blinking should be limited to situations where the user must respond quickly (e.g. alarms) and should disappear upon acknowledgement by the user. Blinking should be applied only for symbols and not for text. Blinking should alternate from high intensity to low intensity and not simply be an on-off blink.

### Brightness

Brightness, or contrast enhancement, should be used to indicate the significance of particular items of information. It enables information to be located more quickly and may be used for indicating:

-	Which items or sequence steps are "active";

-	Which route has been selected in a pipe or electrical network.

As a general guideline it is recommended to use brightness differences only as a layout mechanism.

### Inverse (reverse) video

The ‘inverse video ‘ technique should normally be used for selected items on a display rather than for the whole screen. It should be used for highlighting significant messages, test and data fields.
Inverse video may also be used for data entry.

### Process data representation

Presentation of process data should follow the convention as shown below.

#### Numeric data point

Process data should be displayed right justified, using the following typical conventions:

| Flow | 4 digits and a decimal point (e.g. 1.234, 12.34, 123.4, 1234 t/d, Kt/d) |
| --- | --- |
| Pressure | 3 or 4 digits and a decimal point (e.g. 123.4, 12.3, 1.23 bar, mbar, barA) |
| Temperature | 4 digits and one decimal point (e.g. 123.4 degC) |
| Level | 3 digits and no decimal point (e.g. 100 %) |
| Tank level | 5 digits and no decimal point (e.g. 12345 mm) |
| Controller outputs | 3 digits and no decimal point (e.g. 100%) |

For other process data, such as QMI output, etc., a specific convention may be used.

Tag numbers identifying numeric data points are useful at the unit, sub-unit and detailed display levels but should not be shown at plant overview display levels. Where they are shown in a graphic, consideration should be given to a target which will toggle these tag numbers on / off to reduce the number of items displayed on the screen. This can be achieved by using the inverse video feature.

The following conventions should be applied for controller outputs:

0% controller output means valve closed irrespective of the valve spring action.

100% controller output means valve open irrespective of the valve spring action.

Colours or shaped borders may be considered to distinguish between different data points e.g. flow, level, pressure, temperature etc.

The following data display behaviour should be adopted:

| Normal | Green |
| --- | --- |
| Alarm | Black text on red or yellow, blinking until acknowledged |
| Manual entry | Black text on white (inverse video) |
| Bad value | To the left of the value, black on magenta (inverse video) "U" for unavailable, "L" for last known value, "F" for fault |

#### Bar display

This should be commonly used to represent the level in a vessel, allowing faster recognition of level than reading a numeric data point. It shall be drawn as a simple bar display in the vessel.

The following bar display behaviour should be adopted.

| Normal | Bar green |
| --- | --- |
| Alarm | Bar red or yellow, blinking until acknowledged |
| Bad value | Bar magenta |

#### Short duration trends

These are small single point trend displays of 10 to 15 minutes duration which are drawn within the schematic graphic displays. In unit and sub-unit graphics they are preferred over numeric data points as they provide a short term history of the particular process value being monitored, which is more meaningful than instantaneous data value. They should only be used for key or critical process parameters and a maximum of four should be used per graphic display. It should be possible to toggling the display of these trends on and off, with the default being off when the graphic is called.

### Controller parameters displayed in graphics

At the plant and unit overview display levels, the measured process values (PV’s) are the important operating parameters. Therefore, information displayed with or for a controller at these displays should be limited to the PV’s.

The other parameters such as set point (SP), output and modes (e.g. auto, manual and cascade) should be shown at the (sub) unit and detailed display levels. In addition to PV’s, these parameters may also be shown together with the controller provided they assist the operator in performing his task.

### Labelling

Labels should be used to identify a single data item (e.g. tag number), a group of items or an entire display. Labels should be unique, meaningful and descriptive.

Each graphic display should be provided with a title in the top left-hand part of the display.

Data labels should be clearly distinguished from the data items themselves. Labels should be placed to the left of single items. For repeating items, the label should be placed above the columns of items. Every item should be clearly labelled. It should not be assumed that the user is able to identify individual items on account of past experience. Context plays an important role.

Where a unit (e.g. %, bar) is associated with a particular data field, it should be part of the fixed label instead of having it entered by the user. In crowded data entry displays, auxiliary layout means may be adopted to distinguish labels from data.

### Text

Text should be in lower case, with only the first letter of the first word in a sentence in upper case. Text in lower case reads more easily than text in upper case.

Upper case text should only be used to call attention to certain items or statements and for titles, headings and labels. Text should be left justified. Full (left and right) justification should not be used for legibility reasons.

### Tables

Data presented in tabular form should be aligned vertically. Alphanumeric data should be left justified, and numeric data should be right justified. Where numbers contain decimal places, each number should be given the same number of decimal places. Decimal points in columns of numbers should align vertically. Indentation should be used for sub-classification.

If tables require more space than can reasonably fit on the display screen, the user should be able to scroll the table upwards and downwards, with the column headings remaining at the top of the display screen.

Each column in a table should have a heading which should be easily distinguishable from data in the table (e.g. by case, colour highlighting, underlining etc.). Columns and sub-headings should be arranged to reflect hierarchies and grouping of the data.

The order in which the information in a table is presented should be logical to the user and may depend on:

-	The order in which the user uses the data;

-	The importance of the data to the user;

-	The frequency with which an item is used;
-	time order (newest first or oldest first, as appropriate);
-	alphabetical or numerical order.

### Windows

Windows are useful when there is a need for extra or detailed information to augment the information contained in the current display without having to use another screen or call up another display.

Typical types of standard windows in the DCS’s should include:

Alarm Window: Shows a list of the latest 5 alarms, which can be invoked, from any display through targets configured in the message bar of the screen.

Instrument Window: Shows an instrument faceplate, which can be invoked through targets configured within graphics. It eliminates the need to call up the control group display when adjustments have to be made for an instrument while on a graphic display.

Trend Window: Shows the trend of an instrument, which can be invoked through targets configured within graphics. It eliminates the need to call up the trend group displays when reviewing trends while on a graphic display.

Message/Help Window: Contains messages, which can be used to assist the operator in the performance of his tasks. It can be invoked through configured targets within graphics or can be made to appear automatically once a particular condition is met. It is ideal for providing information for sequence steps or for announcing errors or problems in a sequence.

NOTE:	1.	The above types of window can be shown simultaneously from a graphic display as they have a fixed location and a size, which does not cover the whole area of the screen.

DCS’s shall have full windowing capabilities which can present all other types of displays as windows (e.g. graphic displays, trend displays, etc.) either individually or simultaneously. The windows can be moved, stretched, minimised, maximised and presented either in tile or overlapping arrangement for multiple open windows.

With more than two windows open, the tiled arrangement rather than the overlapping arrangement should be used. In order not to burden the memory load of the operator and to ensure information is legible, the maximum number of windows open at any one time shall be limited to four per CRT.

# Alarms/Events

## Alarm philosophy

Safeguarding- and pre-alarms shall be presented to the operator via the DCS. An alarm management system shall be implemented to achieve the following objectives:

- minimise the number of active alarms

- maximise the information contained in the alarms

- obtain effective presentation of alarms

- The methods to achieve this are indicated below.

## Alarm Management

Alarms shall be configured into logical groups by:

	Unit
	Priority level

An indication of a point in alarm shall be provided on every display.

Common alarms are not used on the DCS, instead each alarm shall be presented to the operator individually.

Alarm prioritisation levels shall be allocated to enable the operator to discriminate between critical and non-critical alarms. These levels shall be:

	Level 1-Shutdown pre-alarms
	Level 2-Shutdown alarms
	Level 3-Operator warning/ Deviation alarms
	Level 4-DCS diagnostic / maintenance level

Priority level for each individual alarm condition shall be configurable.

First failure indication shall be provided for equipment and process related safeguarding alarms in cases where a trip condition may result in a number of subsequent trips.

An ‘Alarm list’ display shall rank active alarms according to priority and time of occurrence.
All occurring alarms within 24 hours shall be presented in one history alarm summary (200 alarms as a minimum shall be presented). The total alarm summary shall be made visible by scrolling. Historic alarms (older than 24 hours) are stored in the historic event file specified below.

Every alarm shall be presented with date and time of occurrence, acknowledge and disappearance.

### Alarm Masking, Inhibit and Disable

An alarm suppression function shall be available to suppress alarms or group of alarms that are not significant at certain times or for certain operation, e.g. for process units or parts thereof which are out of operation and spare equipment not in use.

It shall also be possible to defeat individual alarms or groups of alarms under password or key lock control (supervisor's level).

a)	Masking

Under pre-defined conditions, alarms shall be capable of being masked i.e. cut out. This shall prevent alarms from being reported when alarming would be obvious (such as preventing a low-pressure alarm when the associated pump is off). This 'intelligent' alarming shall be configurable and modifiable by an Engineer without the need for programming knowledge.

The Vendor shall also include masking facilities to suppress annunciation of large numbers of consequential alarms following one incident avoiding superfluous information being presented to the operator.

b)	Inhibit:

Facilities shall be provided for the operator to inhibit and reinstate alarm annunciation for individual or groups of tag numbers. Point(s) which have been inhibited shall not be annunciated but shall still be recorded in the Alarm/Event List.

c)	Disable:

Facilities shall be provided for the operator to disable and reinstate alarm handling for individual or groups of tag numbers. Point(s) that have been disabled shall be ignored by the DCS on occurrence of an alarm condition.

A list of tag numbers and/or groups being masked, inhibited or disabled shall be available on operator command.

The following table defines the actions of each category:

|  | Display | Print | Log |
| --- | --- | --- | --- |
| Enable | Yes | Yes | Yes |
| Masked | No | No | Yes |
| Inhibit | No | No | Yes |
| Disable | No | No | No |

### Alarm Handling

The operator shall be warned of points in alarm as follows:

	Audible alarms

	Display of the highest priority tag for the first alarm activated in an area on top of each display page

### Alarm Acceptance

Alarms shall be accepted at the graphic level, at the alarm summary or alarm group page. On acceptance the alarm Tag/Text and symbol shall be displayed steady in the alarm. On clearing the fault, the alarm shall be deleted from the alarm displays. Once an alarm has been annunciated, the operator using a single ‘acknowledge’ key on any of the console keyboards must individually acknowledged.
The DCS shall not allow an operator to acknowledge an alarm unless the alarm is visible on the respective VDU. On acknowledgement of the alarm, the audible signal shall be silenced if there are no other unacknowledged alarms outstanding.

### Audible Alarms

The DCS should be configured to emit different audible tones corresponding to alarm priority levels for process alarms. In order for process alarms to be easily distinguished, no more than two different auditory tones should be used, as follows:

-	A high pitched continuous tone for high priority alarms;
-	an intermittent tone for medium and low priority alarms.

The tone volume should be adjustable, with the minimum setting above the background noise level in the control room.

NOTES:	1. The audible alarm generated by the hardwired display panel of the FGS should be distinguishable from the process alarm tones configured in the DCS.

There shall be a separate audible alarm silence function which shall allow the operator to silence the audible alarm signal using a single ‘silence’ key on any of the console keyboards without viewing or acknowledging any alarms. The audible signal shall be initiated again, however, when a new alarm has been detected.

### Alarm resolution

All alarms shall be time stamped from the time of occurrence to one-second resolution. The time of occurrence and the time of acceptance shall be printed on the alarm/event printer as well as logged on hard disk.

For alarms transmitted from the SGS, preference is given to a time stamp equal to the scan time of the SGS rather than the scan time of the DCS. So the SGS should transmit its time stamp to the DCS (refer also schedule L-2).

### System Response

All alarms shall be reported to the operator within one second from detection. This time includes transmission to the VDU and presentation to the operator.

### Alarm and Event Logging

The DCS shall provide facilities for the display and storage (on hard disk) of all alarm- and event occurrences. It should be possible to separate presentation of alarms from events. The historic event file should be designed to store the events for 7 days operation.

The storage system shall be sized for 2000 events and 2000 alarms as a minimum.
All events shall be recorded in a ’journal file’ on the hard disk to allow backtracking for analysis after the event has occurred. The file shall automatically overwrite the oldest data when the file is full.
An "Event" is defined as a change of status of a tag point or variable, including an alarm, operator key-board/mouse/trackball action.

# Transmitter Validation

The trip- and control transmitter signals shall be continuously compared. Comparison will be done in the DCS using the standard ‘MVC’ algorithm. A warning will be generated to the operator if differences exceed a certain pre-set level. The signals from trip transmitters will be transmitted via the serial communication link from the SGS to the DCS.  Preferably the ranges for both transmitters shall be the same to avoid nuisance alarms.

# Trending/Reporting

Trend displays shall be line graph representations with variable magnitude shown on the Y-axis and time on the X-axis. It shall be possible to assign any variable e.g. measured value, set point, output, totalisers- and calculated (derived) values of any tag number in the DCS to real time or historical trending. 
It shall be possible to trend either instantaneous or average data for a particular variable.
The scales for process values and time base on a trend shall be operator adjustable.
Time base shall be freely selectable by operator.

## Trend archives

Trend archiving, by means of copying the sample point values to a floppy disk, shall be possible for both real time and historical trend. The data shall have a format to enable import to a database program (spreadsheet) in a DOS\Windows environment.

## Real Time Trends

Real time trends shall feature a minimum sample rate of 2 seconds and a minimum display time of 15 minutes. The sampling rate shall be configurable. It should be possible to show trends of up to 4 variables simultaneously as a minimum.

## Tuning Trend

All individual control loops shall be configured for a tuning trend with time base of 15 minutes with a sampling rate of 1 second.

## Historic trends

It shall be possible to view old trends at the operator station without interrupting the DCS operation.
The minimum sampling rate for historical trend shall be 1 minute or less.

Adequate disc capacity shall be available and allocated for storage of historical data of a time period of 31 days for 1 minute snapshots, hourly averages, shift averages and daily averages, for all points specified.

## Reporting

Pre-formatted reports shall be available on the DCS, allowing screen display and printout of data on freely assignable groups of points. The standard reports shall be supplemented by free-format reports for presentation of data in customised format. Typical data may consist of measured data, calculations, manual entries, historical values etc. from any log. It shall be possible to manipulate the data in order to generate / calculate time-based averages, totalisations, minimum values, minimum times, maximum values, maximum time etc. Report formats and destination (i.e. appointed printer) shall be easily configurable whilst the DCS is on-line. It shall be possible for reports to cover the full width of the printer and one or more pages

All reports shall be available on screen and / or on a printout from the report printer.

As a minimum the following reports shall be provided:

-	daily production report (e.g. totalised values)
-	reservoir off-take reports (e.g. well tests)
-	inspection data( e.g. equipment running hours, starts / stops)
-	summary of operator changes (e.g. set points changes)

Report printout shall be initiated either on:

-	a time interval basis
-	a defined time basis
-	an event
-	an operator command

Defined times or time intervals for reporting shall be configurable to any period of time or time of the day including on the hour, on the half-hour and on the quarter-hour.

# Earthing

Generally the earthing system shall be divided into the following earth types:

	Plant earth (Safety earth)
	Instrument earth (Instrument, screen)

For details refer to schedule L-5 ‘ Instrument Signal Lines’.

# System Availability

The overall design of the DCS shall be such that failure of any component of the DCS shall have minimal adverse effect on the process. Critical loops shall be configured in such a way that the ‘loss’ of one of their components does not impair the overall DCS performance. Critical loops are defined as control loops which have a direct impact on the controllability of the facility and without which the station cannot be operated.

There shall never be a need for a total DCS shutdown for maintenance/repair or upgrade. The DCS shall be designed so that a total loss of essential facilities shall never occur.

- Target DCS availability shall be better than 99.96 % with an MTTR of 8 hours

For the proposed DCS the Vendor shall submit the availability calculations during the design as well as upon delivery of the DCS, with the constraints as mentioned below.

The Vendor shall submit all details of the calculations including the base data used to assess the Vendor's redundancy architecture and the recommendation for spare parts. Any module e.g. tracker ball, CPU, disc unit, I/O module, printer etc. that has an MTBF of less than 10,000 hours shall be separately identified by the Vendor.

The calculations shall be based on:

-	Military Handbook “Reliability Predictions of Electronic Equipment (MIL-HDBK-217E)”
-	the most stringent operating parameters from the environmental conditions specified in the Contract

Equipment reliability figures (i.e. MTBF, MTTR), used for these devices in the calculations shall be based on proven field performance for similar installations as detailed in this specification.

The assumed constraints are:

- All devices not furnished by the Vendor shall be assumed available 100 % of the time.
Failure caused by accidents, fire or other non-equipment related external conditions should not be considered.

- None of the items affecting a task specified in this specification shall be excluded; the failure of one control loop or an analogue I/O of a control function shall be considered as an overall DCS non-availability.

A failure in this context is to be considered for:

	Loss of control over/of one or more controller or control loops.
	Loss of the ability of the operator to view or manipulate the process.

# System Maintainability

The system shall have diagnostic facilities( with associated user procedures) and performance monitoring which will include self diagnostics and a standard diagnostics display library giving statuses on hardware equipment, software, communication gateways and all system failure modes.

The diagnostics shall run continuously as a background task indicating failure of both the primary as well as the hot standby devices and maintain a log of DCS faults and communication performance. The log shall be accessed via standard screen displays from any operator console and shall avoid presentation of faults in the form of error codes.

DCS failures shall be reported as system alarms and all DCS components shall have multiple red and green LED indicators to facilitate the identification of failed cards.

The DCS shall be designed to provide maximum ease of equipment servicing. Any special fixtures or software programs such as card extenders, test circuit boards, test-boxes and associated user procedures shall be provided along with the DCS. Off-line diagnostic software for comprehensive testing of the DCS shall be provided and capable of testing at least the:

-	Input and output modules
-	the communication network
-	serial interfaces
-	all processors (performance and benchmark tests)
-	memory (worst case pattern test and access test)
-	mass storage devices (fixed and removable media)
-	VDU (general operation and alignment patterns)
-	keyboard
-	printer

In addition detection of the following faults, via the main operator interface, is also required:
-	power supply
-	over temperature
-	fan failure (if any)
-	input / output circuitry, incl. fuse failure

# System Immunity

The DCS shall be immune to the following disturbances:

	Variations of power supply +- 10%
	Variation of power supply frequency as specified
	Power supply interruptions up to 500 ms
	Common mode and series mode randomly phase transient over-voltages applied on the mains input from a source of 50 ohms
	Electromagnetic radiation; compliant with IEC-801 and IEC-1000-5 (for total system).

# Warranty Period

The warranty period shall start after the signing and hand-over of Site Acceptance Certificate for a period of one year. It should allow for 24 hrs. Support by vendor’s hard-& software engineers on site (24 hrs) for failure rectification.

# PROJECT REQUIREMENTS

## Functional Design Specification

The Vendor shall prepare, detail, revise and further develop a ‘Functional Design Specification’. This Functional Design Specification shall be submitted for review as one complete document. 
The approved Functional Design Specification shall act as a working document for the detailed engineering and implementation of the DCS.

The Functional Design Specification shall contain the following information as a minimum:

a)	Definition of:
	-	The system objectives
	-	Each party's responsibilities
	-	Specifications and equipment quantities for all deliverable equipment items, 
		giving type, manufacturer etc.
	-	The documentation to be delivered
	-	All spare parts, tools, test equipment and installation materials

b)	Overall system specification including:
-	Dimension, weight, power consumption, heat dissipation, position 
             requirements for all equipment units and the complete system
-	System schematics and equipment layout drawings
-	Analysis of spare capacities and redundancy requirements and the ability to meet the 
            performance criteria e.g. response times, availability etc
-	Analysis of system and communications network load

c)	Drawings including:
	-	Network cabling, system cabling and hook-up drawings, system architecture
	-	Electrical single line and earthing diagrams

d)	Interface Specifications including:
	-	Plant interface specifications
	-	Serial link interface specifications and serial link input/output summary
	-	communications network specifications and definition of transmitted data

e)	For all software to be developed, including application programs:
	-	A block diagram of software structure and program schedule
	-	A software specification including flow charts, detailed descriptions, memory 		            and timing requirements

- Guidelines for configuration:
-	A guideline for configuration of the DCS operator interface including operational procedures, commands, display presentations, hard copy print-outs and reports
-	A guideline for configuration of all data base requirements

g)	Definition of factory and site tests

h)	Procedures dimensions, weights and environmental conditions for:
	-	Installation and commissioning of equipment, cables etc.
	-	Packing, transportation and storage including methods, preliminary quantities,
		dimensions, weights and environmental conditions

The Functional Design Specification shall be developed to include a series of volumes each relating to the various areas of design e.g. Hardware, Software Development, Database, Services.

## Commissioning

### Pre-Commissioning

The Vendor shall:

-	Test all functions of the DCS including tests as specified in the Contract, standard test 	procedures and diagnostic routines
-	Verify DCS program and data load and restart facilities
-	Test and commission the communications network between locations
-	Test and commission all data transmission between locations
-	Simulate, test and commission all input functions from the incoming terminals at the 	marshalling cabinets through to the operator interface
-	Test and commission all output and control functions from the operator interface 
	through to the outgoing terminals at the marshalling cabinets
-	Test and commission the complete database
-	Test and commission the facilities and operator interface including all displays, reports, 	application programs, backups and archiving etc.
-	Test and commission all maintenance and diagnostic facilities

### Final Commissioning, including plant start-up.

The Vendor shall assist in commissioning all field input and output devices to the DCS including:

-	Commissioning from the field device to the operator interface
-	Reconfiguration and rewiring of the DCS where necessary
-	Start-up and shutdown of the DCS
-	A Site Acceptance Test (SAT) to demonstrate that the DCS functions correctly in combination.
            With plant instrumentation and other instrument (sub) systems

Start-up assistance is required from VENDOR and shall be incorporated in his proposal for the following activities:

-	to check whether system installation is conform to Vendor’s specifications;
-	to install system configuration;
-	to power-up the system and run diagnostic programs to ensure hardware integrity.

# FACTORY ACCEPTANCE TEST (FAT)

## General

The DCS including subsystems shall undergo Factory Acceptance Tests (FAT).
The FAT shall be divided into two phases. 
- Phase 1 tests shall be carried out at the Supplier's works. 
- Phase 2 tests (SIT) shall be carried out at the DCS Supplier's works (if applicable).

NOTE: The FAT is performed to demonstrate that all required testing has already been successfully performed by the Supplier. It shall not be used as a substitute for the Supplier's own tests.

During the manufacturing period the Supplier shall perform hardware checks to detect component failures. If any failures are discovered and replacements made, these shall be noted and logged.

The Supplier shall provide adequate personnel, test facilities and test equipment for the FAT.

The Supplier shall provide FAT procedures. These shall include:

-	Timing of activities;

-	Supplier's personnel attending the FAT (with responsibilities);

-	Methods by which deficiencies shall be identified recorded and rectified.

The test procedures shall be made available 6 weeks prior to the FAT.

The Supplier shall notify the SGC 4 weeks in advance of when the system will be ready for FAT. SGC representatives may wish to attend the FATs.

## FAT phase 1

FAT Phase 1 consists of a full functional test performed at the Supplier's works. This phase is to demonstrate with a system functional test, that the operation of the control, monitoring and logic systems included in the equipment package perform as specified.

This phase shall also include visual checks on workmanship, insulation tests and functional tests, including full simulation of all inputs, outputs and logic. Inputs and outputs shall be simulated from the cabinet ‘Elco’ boards.

Final documentation shall be available during this test.

The VENDOR shall provide during FAT a test schedule detailing the activities to be performed. This shall include the timing of activities, Vendor's personnel attending the tests and their responsibilities.

Methods by which deficiencies shall be identified in the test schedule, recorded and rectified. The schedule shall be made available 6 weeks before the FAT. SGC shall be notified at least 3 weeks in advance that the system is ready for the FAT.

VENDOR shall correct any defects, imperfections or deviation from specifications found during test at shortest possible time, after completion of the FAT.

The complete report on the FAT shall be sent to SGC one week after FAT.

## FAT phase 2; System Integration Test (SIT)

FAT Phase 2 includes connection of the ‘other’ sub-systems e.g. SGS, FGS, UCP, CAO etc. to the DCS and testing of the serial communication with the DCS.

The system integrity test shall also include a performance check of the serial communication links with all sub-system. For this purpose, the sub-systems concerned will be shipped, to DCS vendor’s premises, temporarily installed and connected to the DCS. DCS vendor shall also connect the power supply to these systems.

If this integration test is not feasible/practical, then testing shall be done with a representative ‘dummy’ system.

The Sub system supplier is responsible for loading the equipment at the Supplier's works, transporting it to and unloading/loading it at the DCS Supplier's works and for insurance covering the time the system is installed at the DCS Supplier's works.

Punch list items from FAT Phase 1 shall be tested during FAT Phase 2.

During the FAT the Contractor shall ensure that Vendor representatives are present for each individual system to ensure warranty and to conduct modifications to the system design when interface problems are encountered.

## Operational Support

The Vendor shall provide a commissioning engineer on site for the duration of the 30 days continuous trial operation, unless specified otherwise. The commissioning engineer shall be available continuously during normal working hours and on-call outside normal working hours and shall:

-	Rectify any faults in the DCS
-	Provide hands-on training and support to operator / maintenance personnel
-	Advise on maintenance procedures

## Field Support

DCS vendor shall submit details his field service organisation including:

	Availability of field service personnel 24 hours per day at the plant site during start-up
	Field service rate structure, both on-call personnel and full annual maintenance contract basis
	Availability of spare parts to the plant site such as location of spare parts depots 
     and transit time on a normal and on a emergency basis.
	Availability of remote support service and diagnostics by means of modem.

### Remote Diagnostic Service

The DCS vendor shall submit a quote for services covering remote on-line diagnostic features using a dial-in modem. The service shall enable a service centre of the DCS vendor to remotely diagnose the DCS and be able to rectify software related problems on-line or instruct/guide the service engineer on site to resolve hardware related problems.

Proper security measures shall be in place to prevent unauthorised access (e.g. by using dial-back modems) and measures to limit the authority (scope of allowed activities) of the remote service engineer.

## Spare parts

DCS Vendor shall:

·	Supply commissioning / start-up spares.

·	Supply spares and consumables for initial one-year's operation.

·	Provide a detailed listing of recommended spares and consumables for two years' operation.

Fully completed Spare Part and Interchange ability Record forms for all parts of his supply.

Guaranteed turn around times for repair of cards and equipment on return to service centre shall be quoted.

The DCS Supplier shall quote a guaranteed life before obsolescence relating to all components, associated spares, compatible components and back-up services, This shall be a minimum of 10 years.

Spares ordered with equipment shall be included in acceptable test procedure to ensure correct working and compatibility.

## Documentation

The DCS vendor shall provide the manuals/documents/drawings listed below. The information shall reflect ‘as-built’ situation. All drawings shall be produced in AutoCAD® format 2006, or higher, suitable for an IBM PC. Any special fonts, symbol or menu files used to generate the drawings that are not part of the standard AutoCAD release other than through configuration shall also be supplied. All manuals/documents shall be produced in Microsoft Word® for windows ’98.

## Manuals

The following manuals are required:

System manual 
Maintenance manual
Operating manual

The manuals shall include all relevant documentation together with full system and user interface descriptions and procedures appropriate to the manual function.

Manuals shall be available for factory test. The versions shall be in an advanced draft stage requiring amendment only as a result of changes found necessary during the test.

All documentation shall be supplied in English.

For sequence control manuals shall include detailed flow sheets, documented with all relevant (cross) references and clarification notes.

Binary interlocking functions e.g. for conditional (controller) mode switching, etc. shall be documented by means of logic gates in accordance with IEC 617-12.

The information shall reflect the "as-built" situation.

### Operating manual

The operating manual contains:

a.	General information about DCS system
b.	Simple (step-by-step) operating instructions
c.	Background information concerning the facility

### System manual

The system manual will be used by the system engineers and shall detail the relationship between the various parts of the delivered system, engineering instructions and software and hardware descriptions from system and packages.

Typical design information, which should be covered:

-	System description, including standard/optional function blocks, applications, programs

-	System communication links characteristics including communication speed, protocols, access/control principles, error detection/recovery, network logging, failure identification/repair, back-up principles.

- Configuration documents

### Maintenance manual

The maintenance manual shall contain all data necessary for the maintenance of the delivered systems.

It shall cover comprehensively all predictive, preventive and corrective maintenance tasks and detailed procedures required allowing on-site company personnel to maintain the specified availability.

### Drawings

All the drawings required for the design, manufacturing, installation, maintenance and operation of the delivered systems shall be provided, i.e. as a minimum:

a.	Functional design specification
b.	Certified dimensional drawing of all cabinets, operator station and peripherals;
c.	Lay-out drawings of all cabinets, with location details for field I/O terminations;
d.	Power distribution drawings with interconnection details;
e.	Earthing lay-out and connections;	
f.	DCS system cable schedule;
g.	DCS configuration data;	
h.	DCS system interconnection drawings;
i.	Hardwired panel lay-out and construction drawings;
j.	Site planning, production and installation guidelines and details;
k.	List of all the batteries within the DCS;
l.	Factory acceptance test documents
k.	Man/machine interface and supervisory controls
l.	DCS architecture, including all interfaces with sub-systems

# Training

VENDOR shall list in proposal training programs available and minimal required training for the following disciplines:

a.	Maintenance technicians;
b.	plant operators;
c.	system engineers.

It is emphasised that courses offered should be split into these disciplines and structured accordingly.

All training courses shall be in accordance with the specific software release offered in the quotation and related to the equipment and the functionality (configuration) included in the order. Where non-standard equipment is envisaged, the training courses shall adequately cater for these items.