| SYRIAN PETROLEUM COMPANY Specification Sheet Exhibit-G, Data References ###### Site Conditions | Arab Gas Pipeline Project Phase II | RFQ File No. /2022 |
| --- | --- | --- |
| - Project Location - The sites that comprise the Arab Gas Pipeline Project Phase II are located at pipeline rout, which shall connect to Arab Gas Pipeline Project Phase I at AL Foreqls area (about 50 km east of Homs City) at BVS 6011 , extended to Aleppo PRMS(R-7003 ). with Fiscals Metering stations ( FMS ) at Al Foreqls area and compressor units Al Foreqls area . - The data provided in this document shall precede all other data in RFQ tender book. - Meteorological Data Climatic conditions include a dust/sand laden desert atmosphere, with the occasional heavy rain showers. - Design Temperature Maximum Ambient Temperature 52 Degree C Minimum Ambient Temperature -10 Degree C Black Bulb Temperature 82 Degree C Indoor Temperature Maximum 55 Degree C Indoor Temperature Minimum -14 Degree C - Precipitation Average Annual Precipitation 500 mm Maximum 15 minutes Rainfall 30 mm Maximum 24 Hrs Rainfall 100 mm (Brief and severe flash flooding in Wadis) - Wind Maximum Wind Velocity 45 m/s mostly West (Design factor of 1.5 used) 2.4 Earthquake Design for Richter 7 Earthquakes (Zoon 4). 2.5 Humidity Average 20-90 % - Visibility Maximum Visibility Excellent Minimum Visibility 10 m (in Summer due to the dust/sand storm) 2.7 Lightening Intense frequency of strikes during brief thunder strikes |  |  |

### GAS Analysis

The Pipeline System and compressor& Fiscal Metering station ( FMS ) at Foreqls shall be designed to transport two different types of gas, the Egyptian gas and the other is the Syrian gas as showing in the table below .

| COMPONENT | UNITS |  | SYRIAN GAS |  | EGYPTIAN GAS |
| --- | --- | --- | --- | --- | --- |
| N2 | Mole % |  | 2.109 |  | 0.010 |
| CO2 | Mole % |  | 3.176 |  | 0.550 |
| CH4 | Mole % |  | 86.152 |  | 92.240 |
| C2H6 | Mole % |  | 5.544 |  | 4.090 |
| C3H8 | Mole % |  | 2.407 |  | 1.870 |
| I-C4H10 | Mole % |  | 0.219 |  | 0.410 |
| N-C4H10 | Mole % |  | 0.259 |  | 0.430 |
| I-C5H12 | Mole % |  | 0.053 |  | 0.150 |
| N-C5H12 | Mole % |  | 0.038 |  | 0.150 |
| N-C6H14 | Mole % |  | 0.029 |  | 0.050 |
| N-C7H16 | Mole % |  | 0.009 |  | 0.030 |
| N-C8H18 | Mole % |  | 0.003 |  | 0.020 |
| N-C9H20 | Mole % |  | 0.001 |  | --- |
| N-C10H22 | Mole % |  | 0.001 |  | --- |
| TOTAL | Mole % |  | 100 |  | 100 |
| Limits of Specifications: |  |  |  |  |  |
| Sp. Gr. |  |  |  | 0.655 | 0.620 |
| Gross Heating Value |  | BTU/SCF |  | 1046 | 1180 |
| Max (H2S) |  | PPM (Vol.) |  | 22 | 8 |

Notes : contractors shall consider the C6+ AS 50% and C7+ for sizing calculation for the worst case

Design Parameters

Pipeline Design pressure                                                   75     Barg

Pipeline Operating Pressure                                         30 -72  Barg

FMS inlet gas pressure                                                 30 –72 Barg