SCHEDULE SPS -10

PROJECT SPECIFICATION FOR BUILDINGS

TABLE OF CONTENTS

1.0	SCOPE.

2.0	GENERAL

3.0	FOUNDATION

4.0	BUILDING.

5.0	FINISHES.

6.0	REFERENCE SPECIFICATIONS.

1.0	SCOPE.

This specification is intended to define the minimum requirements for the buildings for the ARAB Gas Pipeline project. Three types for building shall used on this project. Block Valve Buildings, Telecom Buildings and FMS Buildings.

2.0	GENERAL

The Block valve building is a secure, naturally ventilated building large enough to house the mainline valve (buried), extended spindle, actuator and Line Break detection unit. It shall have a gravel floor. The remainder of this specification does not apply to this type of building.

The Telecom building is located at the block valve stations, a safe distance from the block valve building.

The FMS building shall be located at the FMS near FOREQLS area .

The Telecom and metering buildings shall house:

-	Electronic equipment.

-	Power distribution boards.

-	Batteries and chargers.

Because of the harsh environmental conditions experienced within the desert, these buildings must be designed to provide a stable, dust-proof environment. This shall be achieved by minimizing diurnal variations through the use of a structure incorporating

-	Thermal resistance (double wall and roof).

-	Defined alignment.

All buildings shall have air-conditioning and ventilation provided.

As a minimum, the following furniture shall be provided in the FMS control room:

-	Work table and chair.

-	Fire extinguisher.

-	Computer’s furniture

3.0	FOUNDATION.

Foundation design shall be suitable for the existing condition of the ground, which shall be well consolidated if necessary.

4.0	BUILDING.

The external sun protection walls shall be constructed using concrete blocks laid in a honeycomb pattern.

The doors and doorframes shall be made of steel. Extra attention shall be paid to dust proofing of doors and door frames. Each door shall be provided with intruder switch and automatic door closure.

5.0	FINISHES.

5.1	Interiors:

Within 	the equipment room, a 50mm mortar screed shall be applied to the floor area. On this shall be laid light gray industrial quality, wall to wall, vinyl with two coats of “off-white” masonry paint.

The battery room shall have acid-resistant ceramic tiles laid on a 50mm mortar screed. A single course of bull-nosed skirting tiles shall be laid at floor level around the walls of the room. The walls shall be covered to a height of 1500 mm with glazed white ceramic tiles.

The ceilings of all rooms shall be finished with two coats of “off-white” masonry paint.

The doors and frames shall be finished with two coats or red oxide and two coats of external quality light blue / gray paint.

5.2	Exteriors.

The foundation periphery shall have three coats of bituminous paint applied to a height of 250mm above grade.

The walls shall have a white color, hand sprayed cement finish applied.

The roof shall be finished with an approved silicon type concrete sealant or water proofing agent.

6.0	REFERENCE SPECIFICATIONS.

Schedule C	-	Concrete Design.

Schedule P	-	Painting.

Schedule C-CP-	Construction Practices for Concrete work.