## SCHEDULE SPS -2

PROJECT SPECIFICATION FOR ELECTRICAL SYSTEM

TABLE OF CONTENTS

1.0	INTRODUCTION

2.0	GENERAL

3.0	SCOPE OF WORK

4.0	SYSTEM DESCRIPTION

5.0	APPLICABLE CODES AND STANDARDS

6.0	DESIGN

7.0	SPARE PARTS REQUIREMENTS

8.0	TEST EQUIPMENT

1-INTRODUCTION

This specification describes the application and the minimum requirements for AC and DC power supplies and systems to be used at Block Valve Stations and Fiscal Metering Station(FMSs) and unit copressor and Buildings for the Arab Gas Pipeline project –phase-II

2-GENERAL

It is envisaged that each “Telecom Building” situated near each of the Block Valve Stations and stations along the pipeline route, and the FMSs and compressor unit  shall be provided with power from the Syrian National Electricity Network (Overhead Power Line).

This shall be achieved by a suitably sized step down transformer mounted on a terminal pole close to the BVSs stations and FMSs and compressor unit  . The Contractor will be responsible for all liaison with the Syrian Power Authority, , in order to obtain a suitable power supply.

Contractor shall also be responsible for any power line extensions to existing power lines and complying with the Authority’s requirements for protection, isolation and tariff metering.

# 3-SCOPE OF WORK

The work includes the design, specification, purchase (including spare parts), installation, testing and commissioning of the complete installation, all in close correlation with the requirements of the systems they will provide power for

# 4-SYSTEM  DESCRIPTION

4.1  Power to BVSs stations telecom buildings shall be by means of a high voltage  power line extension from the nearest electric overhead power line. Power will be transformed to low voltage by means of a HV/ LV step-down pole mounted transformer. Power will be taken into the building by low voltage cable into main distribution board.

4.2  Power to FMSs and compressor unit  Building will either be as per 4.1 above, or by installing the emergency diesel generator . CONTRACTOR’S shall provide all equipment, materials and cabling necessary to connect this supply to the FMSs and compressor unit  building .

4.3	The installation inside each building shall comprise at least of the following:

(a)	Main distribution board

(b)	Building interior lighting and socket outlets

(c)	DC system for Cathodic protection

(d)	DC system for telecommunication and data logging systems

(e)	DC distribution board for (d).

(f)	Area lighting at FMSs and compressor unit

(g)	HVAC and ventilation system at BVSs and FMSs and compressor unit    .

(h)	Batteries system

(a)	Main Distribution Board.

This shall consist of a wall mounted board or self stand alone type with two incomes feeders, for the FMSs building, one from the step down transformer (if feeding from Syrian overhead) and the other from a temporary power diesel generator. The incoming circuits shall be protected by a circuit breaker to provide over-current protection and mechanically interlocked to safeguard against parallel operation of the two power sources.

Outgoing circuits shall be protected with circuit breakers to provide over current protection, however in addition the socket outlet circuit(s) shall have 10-mA earth leakage protection. All outgoing circuit breakers shall be fitted with auxiliary contacts for status monitoring as and when required.

The complete board shall be constructed and braced to withstand the fault level as limited by the transformer or as available at the consumer’s terminals.

(b)     Building Interior Lighting:

Interior lighting shall be in accordance with Schedule F - “Lighting Systems”, however automatic illumination of the emergency lighting shall be inhibited until required by manual demand.

Lighting circuits (main and emergency) shall be controlled by wall switch located next to the door. To avoid inadvertent use of the emergency lights during normal main power operation, the switches will be segregated.

(c)	DC System for Cathodic Protection:

This System shall consist of a controlled/regulated DC current injection with                    control/monitoring/indication housed in a separate wall mounted box. Supply will be from the main LV distribution board. No back-up battery supply is required.

The circuit providing the current for the CP system shall be complete with a current or voltage output control device, as required for proper Cathodic Protection adjustments.

(d)	DC Systems (Excluding Cathodic Protection):

The complete DC system shall consist of two incoming supplies to two x 100% charger/rectifier units, each sized to supply the maximum DC output and also recharge the batteries. Under normal conditions both rectifier/battery sets will be on load simultaneously. Loss of AC supply and DC output failure shall be monitored and transmitted with other signals to the RAYAN SCADA system.

(e) 	DC Distribution Board:

This board shall have a DC incoming circuit from each rectifier/battery unit.

Where the DC system is unearthed, all outgoing circuits shall be provided  with earth fault indicating relays and the main DC bus bar shall have an earth fault alarm relay. These relays shall be fitted with auxiliary contacts for remote indication. Outgoing circuits shall be provided with DC circuit breakers for over current protection.

(f) Area Lighting:

Area lighting shall be in accordance with the RFQ specifications.

(g) HVAC:

Air conditioning shall be in accordance with RFQ specifications.

(h) Batteries:

These shall be of the sealed type for long life offering free of maintenance. Each battery string shall be capable of providing half the load for back-up time specified.

The cell connectors shall be provided with hard PVC covers. Cells shall be arranged in banks to afford easy maintenance and battery cleaning. Metal racks shall be provided with lugs for bonding to the system earth.

4.4      Alarm and Monitoring:

The complete system shall be provided for local status indication with abnormal or fault condition alarm indicators, as well as status/alarm signals to be transmitted to the RAYAN SCADA system.

5-APPLICABLE CODES AND STANDARDS:

The equipment shall comply with the applicable RFQ specifications and                                                  international codes and standards

6-DESIGN:

6.1	The systems of BVSs shall be designed for unattended operation.

6.2	The nominal system voltages shall be as stated in Schedules HH and the function Specifications. The battery back-up times shall be as per the Functional Specifications. The allowable upper-and lower voltage limit at the outgoing circuits shall be as dictated by the connected equipment’s manufacturer.

6.3      All equipment will be installed indoors, except the outdoor lighting system.

6.4	The environmental data are:

A desert area, with a dust and sand laded atmosphere.

Occasional heavy showers and severe brief thunder storms.

Maximum average temperature 	:	52 Degree C.

Minimum temperature 		:	-10 degree C.

Prevailing wind direction		:	west

Max. Wind velocity			:	35 m/sec.

Max. Visibility				:	excellent.

Min. Visibility				:	<15 m

When exposed to direct sun radiation materials may reach a black bulb temperature of  82-Degree C..

Relative humidity	:	10% to 90%

6.5    The power system must be designed to meet the Cathodic protection power demand, which is expected to be gradually increasing. The design figure shall be the expected demand after 20 (twenty) years of service of the pipelines.

7 -SPARE PARTS:

Spare parts shall be provided for two (2) years operation of all equipment. The spare parts shall be provided in accordance with the equipment Manufacturer’s recommendations. Parts shall include those recommended by sub-suppliers, as well as those of the primary equipment manufacturer’s.

Consumable spares shall be provided to operate the system for two years. This shall include but not be limited to fuses, lamps and storage cells.

8-TEST EQUIPMENT:

Test equipment as recommended by the manufacturer to provide field maintenance                                on the equipment including items supplied by subcontractors shall be included in                                 the supply