SCHEDULE SPS-3

PROJECT SPECIFICATION FOR TELECOMMUNICATION SYSTEM

TABLE OF CONTENTS

1.0	SCOP.

2.0	TELECOMMUNICATION SYSTEM

3.0	FIBER OPTIC CABLE, AND EQUIPMENT.

4.0	BLOCK VALVE STATIONS.

5.0	SOLAR POWER SYSTEM.

6.0	PRESSURE REDUCTION AND METERING STATIONS.

7.0	CHANNEL ALLOCATION.

8.0	SUPERVISORY SYSTEM.

9.0	BATTERIES.

10.0	EARTHING.

11.0	TEST AND MAINTENANCE EQUIPMENT.

1.0	SCOP.

This specification is intended to define the minimum requirements necessary to provide a telecommunications system linking the different locations related to the ARAB GAS PIPE LINE - PHASE II and to fully interface and integrate this system with the existing system at Gas Coordination Center.

The PROJECT consists of   but not limited to the following:

The system to be provided is intended to carry telephone and telemetry / Data transfer between the Gas Coordination Center and ALFOREQLS FMS -BVS6013- BVS6014-S 6015-BVS6016-BVS6017-R 6018.

All telemetry/data should be transferred to Gas Coordination Center.

All telemetry/data from BVS's, should be transferred to the ALFOREQLS  FMS.

All telephone lines should be transferred from FMS to All BVS-intermediate station and Gas Coordination Center.

The bidder shall utilize (if no other way) the services of Granger telecom and Optilan, the supplier of the original system, to ensure full compatibility.

In General, the work includes the detailed engineering, the material supply, the erection, commissioning, testing, training, and supply of documentation and spare parts.

The system shall be supplied completely ready for start-up even though the minor parts or work are not expressly mentioned in the specifications.

The system shall be designed and supplied in such a way, that it can easily be expanded for future extensions.

2.0	TELECOMMUNICATION SYSTEM

2.1	The communication system to be established shall use a fiber optic cable (24 fibers cable) as the main backbone, to be laid with the Gas pipeline between gas coordination center area and the Syrian Turkish border.

3.0	FIBER OPTIC CABLE AND EQUIPMENT.

3.1	The fiber optic cable shall be suitable for direct buried applications and shall have a minimum of 24 fibers. Two fibers shall be used for this project to transmit the optical signal, leaving the other 22 fibers as spare.

3.2	The fiber optic cable and equipment shall be suitable to cover a minimum distance equal to the maximum distance between 3 succeeding block valve stations without a

Repeater, at SDH STM-1(155.52 Mbit/s). Each BVS installation shall include a fiber optic patch panel terminating all 24 fibers and allowing station bypasses and crosses fiber patching.

3.3	Contractor shall provide detailed power budgets for the system to verify system gain. Provision shall be made for sufficient gain per section to allow for one field repair of two joints and still allow for BVS bypass.

3.4	Installed spare shelf shall be provided for installation FXO, FXS, V24\28 card to full STN-1(155.52Mb/s) capacity and suitable to be upgraded to STM-4 (622Mb/s).

  - Repeaters/drop-insert equipment shall be installed in a telecommunication building at the BVS's and shall be fed via a link to the Syrian Power Grid. The telecommunications equipment shall operate at dual 48 VDC (positive earth).

4.0	TELECOMMS BUILDINGS AT BLOCK VALVE STATIONS.

4.1	A telecomm. Building shall be provided at a non hazardous location within each BVS area. The following equipment shall be installed in this building:

-	Cathodic protection equipment.

-	Batteries, rectifier/chargers, distribution boards.

- 	Fiber Optic equipment.

4.2	The supervisory system provided shall have sufficient capacity to service all alarm points in the system and shall be linked and interfaced to the under construction supervisory system of Gas coordination center.

However, the total design capacity shall be such that if the system is fully equipped the supervisory system shall be capable of being expanded to accommodate all alarms by the addition of extra cards or modules.

5.0	POWER SYSTEM.

5.1	An electrical power system shall be provided at the telecommunication building near some of BVS's. This system is basically designed for feeding the cathodic protection (CP) equipment, and the telecommunication and control equipment. In case the battery voltage drops below a pre-set value, the power supply to the (CP) equipment shall be switched-off automatically and shall be reset manually. Failure of the AC supply and failure of the DC battery back up shall be transmitted to the DCS system.

5.2	Where commercial power is available, the telecommunication equipment shall be fed from a rectifier unit with battery back up, in accordance with Administration specification Schedule “F”.

6.0	FISCAL METERING STATIONS.

6.1	the FMS's  Stations shall be installed at the end of 36” pipeline.

FMS's data and system failures shall be transmitted to the DCS systems.

6.2	To avoid conflicts in earthing polarity and differing operation profiles of the telecom. and Cathodic protection, separate power systems shall be provided for each system. All provisions of the specification shall apply to both systems.

6.3	Where telecom. Cables extend from a BVS - FMS – RECIVER- LAUNCHER- INTERMEDIATE STATIONS and Gas Coordination Center, then adequate lightning and voltage surge protection shall be provided on each pair of the cable.

7.0	CHANNEL ALLOCATION.

7.1	Fully equipped provisions, including additional drop and insert equipment at the BVS's, FMS's. Intermediate stations, launchers, receivers, and THE SYRIAN TURKISH BORDER shall be provided for a total of 63 E1, leaving the other of 155.52Mb/s as spare (we can putted in service with out any adding new configuration or additional soft wear)  .

7.2	Contractor shall prepare a detailed channel allocation plan.

7.3	The following is the minimum channel requirements:

-	Telephone line (Tow at each BVS, launcher, receiver, Intermediate stations, the Syrian Turkish border and ten at each FMS) from the Gas coordination center.

-	Four wire E and M channel for future VHF radio connection.

-	Telecommunication engineering service channel (order wire).

-	Telecontrol/telemetry circuit for remote open/closed indication for the Block Valve status, door open alarm, system failure alarms and alarms from all auxiliary equipment such as battery chargers and charger state indicators

8.0	FIBER OPTIC SUPERVISORY SYSTEM.

Contractor shall supply a network supervisory system for remote supervision of the fiber optic network.

This shall be displayed at any location and shall be interfaced to the under construction supervisory system. A printer shall be provided for logging

9.0	BATTERIES.

The batteries supplied shall be suitable for float charge operation. Battery design capacity shall be such as to ensure a minimum of 48 hrs operation of the station subsequent to mains

Failure. Contractor shall supply load calculations to support the capacity supplied. The battery shall be supplied, configured as two banks to allow independent operation under one bank during maintenance operations. Battery charger shall be duplicated with each charger

Having sufficient capacity to operate the system and maintain battery charge. Automatic balanced load sharing shall apply during dual operation.

10.0	EARTHING.

10.1	Contractor shall provide a dedicated earth system for the Telecom. Equipment at each site. The maximum earth resistance measured under normal summer conditions shall be ten (10) ohms.

10.2	Contractor shall examine the relationship between the cathodic protection for the pipeline and the earthing requirement for the fiber optic cable. He shall clearly identify any problems associated with voltage differentials between the fiber optic cable armoring and the pipeline and minimize such problems.

11.0	TEST AND MAINTENANCE EQUIPMENT.

Contractor shall supply and provide test and maintenance equipment as recommended by the manufacturer to provide field maintenance on the equipment.