SPS-5	Specification of ESD System

SCHEDULE SPS-5

PROJECT SPECIFICATION FOR ESD SYSTEMS

TABLE OF CONTENTS

1.0	SCOPE OF WORK.

2.0	ESD SYSTEM.

1.0	SCOPE OF WORK.

This specification is intended to define the minimum requirements of the ESD system for the ARAB Gas Pipeline project phase II.

2.0	ESD SYSTEM

.

2.1	ESD system shall only be provided at the Fiscal Metering Stations (FMS).

2.2	Remote closing of the block valves at BVS's, line’s SDV and emergency stop gas compressor from the DCS system and from the GCC shall be provided as well.

2.3	Shutdowns shall be initiated manually or automatically.

  - The Station Emergency Shutdown (ESD) shall be initiated as

Minimum at:

- Manual push buttons located in, control room, Main exit gate, metering

Trains area and the Inlet /Outlet Station area, Gas compressor area etc…

- High high instrument gas pressure.

- Low low instrument gas pressure.

- Gas/Fire detection signal in control room.

- Remote ESD from GCC.

- Etc.

A station Emergency Shutdown (ESD) shall cause the following actions:

-	Depressurization of the station gas supply to the flare.

-	Closing of the slam-shut valves.

  - Automatic shutdown of each metering trains, gas

Compressor station without de-Pressurization (PSD) at the FMS's

Shall take place as minimum at:

- High high fuel gas pressure to compressors.

- Gas compressor failure.

- High high liquid level in the main filters/separators

2.6	Line Break Detection signal shall initiate a shutdown signal to DCS systems, causing the up-stream and down-stream block valves of the detected unit to close automatically, re-opening of the block valves shall be initiated just manually (locally). The main valve at BVS in which line break is detected shall close automatically by unit mechanism.

2.7	The design shall ensure that an individual train (PSD),or active compressor(s) failure  shall shut only that train’s SDV or compressor(s) and not the station ESD.

2.8 	After a shutdown, the station or train has to be reset manually.